## 年間集計
20181106建物全体テスト改訂トライアル結果集計.xlsx | [9 empty] | 2019-01-07
|  |  |  | 小野委員 | 矢島委員 | 伊藤委員 | 品川委員 | 二宮委員2 | 富樫委員 | 宮田委員
|  |  |  | NewHASP |  | BEST |  |  | Popolo | E+ | tool1 | tool2 | tool3
|  |  |  | A | B | C | D | E | F | G
建物全体 | 積算負荷 | MWh | 冷房顕熱 | 512.9302 | 588.5244 |  | 582.4679 | 489.9708 | 497.356 | 614.9099
|  |  | 冷房潜熱 | 112.2048 | 109.4343 |  | 93.2498 | 93.8867 | 83.5827 | 101.0917
|  |  | 暖房顕熱 | -139.3718 | -105.5774 |  | -100.2375 | -134.0307 | -163.4955 | -74.1266
|  |  | 暖房潜熱 | -6.7411 | -4.0793 |  | -10.264 | -11.0788 | -8.106 | -24.8532
|  | MJ/m2年 | Cooling-sensible | 212.7293 | 244.0807 |  | 241.5626 | 203.2073 | 206.2701 | 255.0237
|  |  | Cooling-latent | 46.5351 | 45.3861 |  | 38.6728 | 38.938 | 34.6645 | 41.9261
|  |  | Heating-sensible | -57.8021 | -43.7865 |  | -41.5708 | -55.587 | -67.807 | -30.7428
|  |  | Heating-latent | -2.7957 | -1.6918 |  | -4.2567 | -4.5947 | -3.3618 | -10.3074
| 最大負荷 | kW | 冷房顕熱 | 694.3291 | 1129.763 |  | 676.8257 | 803.773 | 1026.0847 | 546.607
|  |  | 冷房潜熱 | 168.5633 | 173.3893 |  | 305.9305 | 357.4851 | 255.7281 | 300.2446
|  |  | 暖房顕熱 | -1078.2679 | -1097.9208 |  | -518.5402 | -946.5349 | -1382.702 | -364.135
|  |  | 暖房潜熱 | -42.8922 | -85.8008 |  | -83.4417 | -125.9311 | -167.4402 | -434.1938
|  | W/m2 | 冷房顕熱 | 79.9893 | 130.1529 |  | 77.9708 | 92.5976 | 118.2088 | 62.9712
|  |  | 冷房潜熱 | 19.4191 | 19.9751 |  | 35.2434 | 41.1836 | 29.4608 | 34.5893
|  |  | 暖房顕熱 | -124.2205 | -126.4846 |  | -59.7362 | -109.0443 | -159.2924 | -41.9497
|  |  | 暖房潜熱 | -4.9413 | -9.8846 |  | -9.6125 | -14.5077 | -19.2897 | -50.0207
----1F_廊下----
1F廊下 | 積算負荷 | MWh | 冷房顕熱 | 2.1402 | 2.2735 |  | 2.5689 | 2.2276 | 2.9326 | 3.3441
|  |  | 冷房潜熱 | 0.25297 | 0.018418 |  | 0.26446 | 0.22663 | 0.37758 | 0.56312
|  |  | 暖房顕熱 | -9.0782 | -4.7723 |  | -8.5744 | -6.5229 | -8.7005 | -9.3981
|  |  | 暖房潜熱 | -0.32012 | -0.021658 |  | -0.30815 | -0.26991 | -0.43978 | -1.737
|  | MJ/m2年 | 冷房顕熱 | 47.1233 | 50.0594 |  | 56.5625 | 49.0479 | 64.5711 | 73.6306
|  |  | 冷房潜熱 | 5.5699 | 0.40553 |  | 5.8229 | 4.9901 | 8.3138 | 12.399
|  |  | 暖房顕熱 | -199.8875 | -105.0779 |  | -188.7938 | -143.6244 | -191.5701 | -206.93
|  |  | 暖房潜熱 | -7.0484 | -0.47686 |  | -6.785 | -5.9431 | -9.6833 | -38.2465
| 最大負荷 | kW | 冷房顕熱 | 6.6381 | 2.7504 |  | 8.8715 | 7.2835 | 6.2328 | 11.3657
|  |  | 冷房潜熱 | 2.3871 | 0.7488 |  | 2.7762 | 3.2702 | 4.6332 | 6.8626
|  |  | 暖房顕熱 | -21.0752 | -9.8064 |  | -18.3905 | -15.6038 | -22.1024 | -22.4853
|  |  | 暖房潜熱 | -1.0137 | -0.6048 |  | -1.5958 | -1.8907 | -3.9793 | -14.3623
|  | W/m2 | 冷房顕熱 | 40.6 | 16.822 |  | 54.26 | 44.5475 | 38.1208 | 69.5153
|  |  | 冷房潜熱 | 14.6 | 4.5798 |  | 16.98 | 20.0015 | 28.3377 | 41.9728
|  |  | 暖房顕熱 | -128.9 | -59.978 |  | -112.48 | -95.4363 | -135.1829 | -137.5248
|  |  | 暖房潜熱 | -6.2 | -3.6991 |  | -9.76 | -11.564 | -24.3383 | -87.8425
----1F_ロビー----
1Fロビー | 積算負荷 | MWh | 冷房顕熱 | 2.8817 | 2.4384 |  | 5.0885 | 4.6349 | 2.0532 | 2.8611
|  |  | 冷房潜熱 | 0.22519 | 0.01268 |  | 0.23617 | 0.15343 | 0.26221 | 1.7852
|  |  | 暖房顕熱 | -2.6431 | -3.0729 |  | -1.971 | -1.81 | -6.1413 | -4.6704
|  |  | 暖房潜熱 | -0.28594 | -0.0149 |  | -0.27491 | -0.19731 | -0.30541 | -0.4338
|  | MJ/m2年 | 冷房顕熱 | 103.7398 | 87.7824 |  | 183.1848 | 166.8573 | 73.9169 | 103.001
|  |  | 冷房潜熱 | 8.1068 | 0.45648 |  | 8.5022 | 5.5234 | 9.4396 | 64.2661 |  |  |  | 図1 建物全体（積算負荷）
|  |  | 暖房顕熱 | -95.1534 | -110.6258 |  | -70.9564 | -65.1589 | -221.0874 | -168.1327
|  |  | 暖房潜熱 | -10.2938 | -0.5364 |  | -9.8968 | -7.103 | -10.9946 | -15.6168
| 最大負荷 | kW | 冷房顕熱 | 4.9 | 4.63 |  | 8.442 | 8.004 | 4.5047 | 7.9344
|  |  | 冷房潜熱 | 2.15 | 0.66 |  | 2.515 | 4.84 | 3.2175 | 6.6818
|  |  | 暖房顕熱 | -9.79 | -15.24 |  | -8.363 | -10.186 | -13.7004 | -13.8961
|  |  | 暖房潜熱 | -0.91 | -0.42 |  | -0.756 | -1.545 | -2.7634 | -8.175
|  | W/m2 | 冷房顕熱 | 49 | 46.3 |  | 84.42 | 80.04 | 45.0468 | 79.344
|  |  | 冷房潜熱 | 21.5 | 6.6 |  | 25.15 | 48.4 | 32.1751 | 66.8182
|  |  | 暖房顕熱 | -97.9 | -152.4 |  | -83.63 | -101.86 | -137.0038 | -138.9615
|  |  | 暖房潜熱 | -9.1 | -4.2 |  | -7.56 | -15.45 | -27.6341 | -81.7503
----1F_EVホール----
1FEVホール | 積算負荷 | MWh | 冷房顕熱 | 0.18407 | 0.18278 |  | 0.22449 | 0.23849 | 0.28589 | 0.30064
|  |  | 冷房潜熱 | 0.027023 | 0.00153 |  | 0.028341 | 0.13878 | 0.031465 | 0.064231
|  |  | 暖房顕熱 | -1.1557 | -0.67396 |  | -1.1414 | -1.3173 | -1.0904 | -1.0474
|  |  | 暖房潜熱 | -0.034313 | -0.0017964 |  | -0.032989 | -0.16221 | -0.036649 | -0.1813
|  | MJ/m2年 | 冷房顕熱 | 55.2197 | 54.8334 |  | 67.3482 | 71.5475 | 85.7676 | 90.1917
|  |  | 冷房潜熱 | 8.1068 | 0.459 |  | 8.5022 | 41.6349 | 9.4396 | 19.2694
|  |  | 暖房顕熱 | -346.7023 | -202.1872 |  | -342.4223 | -395.2049 | -327.1333 | -314.2297
|  |  | 暖房潜熱 | -10.2938 | -0.53892 |  | -9.8968 | -48.6632 | -10.9946 | -54.3902
| 最大負荷 | kW | 冷房顕熱 | 0.6984 | 0.534 |  | 0.92592 | 0.9036 | 0.67626 | 1.1119
|  |  | 冷房潜熱 | 0.2544 | 0.1236 |  | 0.29712 | 0.39744 | 0.3861 | 0.79083
|  |  | 暖房顕熱 | -2.3556 | -1.0644 |  | -2.194 | -2.3372 | -2.4735 | -2.1686
|  |  | 暖房潜熱 | -0.1092 | -0.0504 |  | -0.17076 | -0.2298 | -0.33161 | -1.3012
|  | W/m2 | 冷房顕熱 | 58.2 | 44.5 |  | 77.16 | 75.3 | 56.3546 | 92.6609
|  |  | 冷房潜熱 | 21.2 | 10.3 |  | 24.76 | 33.12 | 32.1751 | 65.9024
|  |  | 暖房顕熱 | -196.3 | -88.7 |  | -182.83 | -194.77 | -206.1213 | -180.7181
|  |  | 暖房潜熱 | -9.1 | -4.2 |  | -14.23 | -19.15 | -27.6341 | -108.4344
|  |  |  | 0 |  |  |  |  | 0 | ----1F_中央監視室----
1F中央監視室 | 積算負荷 | MWh | 冷房顕熱 | 13.2431 | 9.9254 |  | 14.0785 | 12.926 | 9.748 | 16.4421
|  |  | 冷房潜熱 | 2.5761 | 1.776 |  | 2.0775 | 2.361 | 1.8414 | 2.1263
|  |  | 暖房顕熱 | -0.03558 | 0 |  | -0.058965 | -0.07062 | -0.91216 | -0.73129
|  |  | 暖房潜熱 | 0 | 0 |  | -0.00024297 | 0.029771 | -0.00033837 | -0.23028
|  | MJ/m2年 | 冷房顕熱 | 1222.443 | 916.1863 |  | 1299.5565 | 1193.1663 | 899.8166 | 1517.7286
|  |  | 冷房潜熱 | 237.7962 | 163.94 |  | 191.7688 | 217.9402 | 169.9793 | 196.276
|  |  | 暖房顕熱 | -3.2843 | 0 |  | -5.4429 | -6.5188 | -84.1993 | -67.5041
|  |  | 暖房潜熱 | 0 | #DIV/0! |  | -0.022428 | 2.7481 | -0.031234 | -21.2564
| 最大負荷 | kW | 冷房顕熱 | 3.7284 | 7.6401 |  | 4.2444 | 3.8017 | 3.8285 | 9.4942
|  |  | 冷房潜熱 | 0.4914 | 3.5061 |  | 0.48984 | 0.49725 | 0.57785 | 1.547 |  |  |  | 図2 建物全体（最大負荷）
|  |  | 暖房顕熱 | -0.4134 | 0 |  | -0.5265 | -0.58422 | -1.536 | -2.6362
|  |  | 暖房潜熱 | 0 | 0 |  | 0.10023 | 0.10452 | -0.30203 | -1.9832
|  | W/m2 | 冷房顕熱 | 95.6 | 195.9 |  | 108.83 | 97.48 | 98.1669 | 243.4401
|  |  | 冷房潜熱 | 12.6 | 89.9 |  | 12.56 | 12.75 | 14.8165 | 39.6672
|  |  | 暖房顕熱 | -10.6 | 0 |  | -13.5 | -14.98 | -39.3836 | -67.594
|  |  | 暖房潜熱 | 0 | #DIV/0! |  | 2.57 | 2.68 | -7.7443 | -50.8512
----1F_更衣室1----
1F更衣室1 | 積算負荷 | MWh | 冷房顕熱 | 0.28122 | 0.38761 |  | 0.42466 | 0.37564 | 0.40326 | 0.42624
|  |  | 冷房潜熱 | 0.2837 | 0.28816 |  | 0.21868 | 0.18743 | 0.21669 | 0.24002
|  |  | 暖房顕熱 | -0.25783 | -0.13086 |  | -0.18569 | -0.21386 | -0.39868 | -0.63812
|  |  | 暖房潜熱 | -0.00013392 | -1.742e-05 |  | -0.0026411 | 0.025688 | -0.014629 | -0.062035
|  | MJ/m2年 | 冷房顕熱 | 92.9855 | 128.164 |  | 140.254 | 124.0636 | 133.3401 | 140.7769
|  |  | 冷房潜熱 | 93.8052 | 95.2808 |  | 72.2262 | 61.9044 | 71.6493 | 79.2729
|  |  | 暖房顕熱 | -85.2538 | -43.2691 |  | -61.3297 | -70.6329 | -131.8244 | -210.7552
|  |  | 暖房潜熱 | -0.04428 | -0.00576 |  | -0.87228 | 8.4842 | -4.8371 | -20.4887
| 最大負荷 | kW | 冷房顕熱 | 0.5999 | 0.45728 |  | 0.83036 | 0.76747 | 0.9625 | 0.79676
|  |  | 冷房潜熱 | 0.24932 | 0.13936 |  | 0.47568 | 0.47502 | 0.35071 | 0.82409
|  |  | 暖房顕熱 | -2.0164 | -0.92762 |  | -1.3997 | -1.5543 | -3.1268 | -1.5995
|  |  | 暖房潜熱 | 0 | 0 |  | -0.075319 | -0.14508 | -0.30121 | -1.0363
|  | W/m2 | 冷房顕熱 | 55.1 | 42 |  | 76.18 | 70.41 | 88.4042 | 73.0973
|  |  | 冷房潜熱 | 22.9 | 12.8 |  | 43.64 | 43.58 | 32.2121 | 75.6048 |  |  |  | 図3 1F廊下（積算負荷） | 図4 1F廊下（最大負荷）
|  |  | 暖房顕熱 | -185.2 | -85.2 |  | -128.41 | -142.6 | -287.1956 | -146.7403
|  |  | 暖房潜熱 | 0 | #DIV/0! |  | -6.91 | -13.31 | -27.6659 | -95.0738
----1F_更衣室2----
1F更衣室2 | 積算負荷 | MWh | 冷房顕熱 | 0.252 | 0.34035 |  | 0.41034 | 0.34044 | 0.43602 | 0.46701
|  |  | 冷房潜熱 | 0.2837 | 0.28816 |  | 0.21866 | 0.1728 | 0.21669 | 0.21807
|  |  | 暖房顕熱 | -0.34392 | -0.23193 |  | -0.22844 | -0.26572 | -0.41514 | -0.67067
|  |  | 暖房潜熱 | -0.00013392 | -1.742e-05 |  | -0.0023143 | 0.040694 | -0.014629 | -0.022003
|  | MJ/m2年 | 冷房顕熱 | 83.3238 | 112.5396 |  | 135.5252 | 112.4373 | 144.1716 | 154.2429
|  |  | 冷房潜熱 | 93.8052 | 95.2808 |  | 72.2167 | 57.0707 | 71.6493 | 72.0243
|  |  | 暖房顕熱 | -113.719 | -76.6876 |  | -75.4495 | -87.7604 | -137.2664 | -221.5058
|  |  | 暖房潜熱 | -0.04428 | -0.00576 |  | -0.76435 | 13.4404 | -4.8371 | -7.2671
| 最大負荷 | kW | 冷房顕熱 | 0.47034 | 0.45074 |  | 0.73728 | 0.64245 | 0.96127 | 0.83191
|  |  | 冷房潜熱 | 0.24932 | 0.12738 |  | 0.46641 | 0.46129 | 0.35071 | 0.94993
|  |  | 暖房顕熱 | -1.5885 | -1.1639 |  | -1.0698 | -1.1758 | -2.7188 | -2.1042
|  |  | 暖房潜熱 | 0 | 0 |  | -0.051884 | -0.12241 | -0.30121 | -0.90379
|  | W/m2 | 冷房顕熱 | 43.2 | 41.4 |  | 67.64 | 58.94 | 88.2914 | 76.3218
|  |  | 冷房潜熱 | 22.9 | 11.7 |  | 42.79 | 42.32 | 32.2121 | 87.1498 |  |  |  | 図5 1Fロビー（積算負荷） | 図6 1Fロビー（最大負荷）
|  |  | 暖房顕熱 | -145.9 | -106.9 |  | -98.15 | -107.87 | -249.7169 | -193.0497
|  |  | 暖房潜熱 | 0 | #DIV/0! |  | -4.76 | -11.23 | -27.6659 | -82.9169
----1F_休憩室----
1F休憩室 | 積算負荷 | MWh | 冷房顕熱 | 0.5749 | 0.77825 |  | 0.88017 | 0.82657 | 0.85706 | 0.91671
|  |  | 冷房潜熱 | 0.56739 | 0.57632 |  | 0.44056 | 0.39539 | 0.43338 | 0.43791
|  |  | 暖房顕熱 | -0.42317 | -0.25902 |  | -0.26344 | -0.2905 | -0.69247 | -0.90624
|  |  | 暖房潜熱 | -0.00026783 | -3.484e-05 |  | -0.0047223 | 0.035977 | -0.029258 | -0.043124
|  | MJ/m2年 | 冷房顕熱 | 95.0465 | 128.6651 |  | 145.3497 | 136.4978 | 141.6951 | 151.3835
|  |  | 冷房潜熱 | 93.8052 | 95.2808 |  | 72.7533 | 65.2935 | 71.6493 | 72.3158
|  |  | 暖房顕熱 | -69.962 | -42.8224 |  | -43.5039 | -47.9726 | -114.4845 | -149.6538
|  |  | 暖房潜熱 | -0.04428 | -0.00576 |  | -0.77983 | 5.9412 | -4.8371 | -7.1214
| 最大負荷 | kW | 冷房顕熱 | 1.0844 | 0.88407 |  | 1.5875 | 1.4506 | 1.8889 | 1.5102
|  |  | 冷房潜熱 | 0.49865 | 0.25477 |  | 0.95048 | 0.94656 | 0.70142 | 1.6462
|  |  | 暖房顕熱 | -3.3338 | -2.0991 |  | -2.2371 | -2.5332 | -5.6984 | -2.6769
|  |  | 暖房潜熱 | 0 | 0 |  | -0.12273 | -0.18007 | -0.60242 | -1.6436
|  | W/m2 | 冷房顕熱 | 49.8 | 40.6 |  | 72.82 | 66.54 | 86.7449 | 69.2731
|  |  | 冷房潜熱 | 22.9 | 11.7 |  | 43.6 | 43.42 | 32.2121 | 75.5151 |  |  |  | 図7 1FEVホール（積算負荷） | 図8 1FEVホール（最大負荷）
|  |  | 暖房顕熱 | -153.1 | -96.4 |  | -102.62 | -116.2 | -261.6946 | -122.7916
|  |  | 暖房潜熱 | 0 | #DIV/0! |  | -5.63 | -8.26 | -27.6659 | -75.3957
----1F_自販機コーナー----
1F自販機ｺｰﾅｰ | 積算負荷 | MWh | 冷房顕熱 | 0.31853 | 0.38159 |  | 0.39849 | 0.38853 | 0.34452 | 0.48285
|  |  | 冷房潜熱 | 0.036464 | 0.028824 |  | 0.038252 | 0.036774 | 0.057162 | 0.096136
|  |  | 暖房顕熱 | -1.4083 | -1.1502 |  | -1.3116 | -1.2749 | -1.6577 | -1.7615
|  |  | 暖房潜熱 | -0.046198 | -0.036125 |  | -0.044529 | -0.043919 | -0.066578 | -0.20136
|  | MJ/m2年 | 冷房顕熱 | 52.6615 | 63.0864 |  | 65.8063 | 64.1606 | 56.958 | 79.7374
|  |  | 冷房潜熱 | 6.0286 | 4.7653 |  | 6.3168 | 6.0727 | 9.4504 | 15.8756
|  |  | 暖房顕熱 | -232.8278 | -190.157 |  | -216.5907 | -210.5369 | -274.0589 | -290.8938
|  |  | 暖房潜熱 | -7.6378 | -5.9724 |  | -7.3534 | -7.2527 | -11.0072 | -33.2529
| 最大負荷 | kW | 冷房顕熱 | 1.0365 | 0.51825 |  | 1.3187 | 1.2962 | 0.84335 | 1.8142
|  |  | 冷房潜熱 | 0.34404 | 0.19162 |  | 0.4009 | 0.53628 | 0.70142 | 1.0289
|  |  | 暖房顕熱 | -3.3773 | -2.012 |  | -2.9365 | -3.0572 | -3.5396 | -4.6008
|  |  | 暖房潜熱 | -0.14589 | -0.11759 |  | -0.23043 | -0.31 | -0.60242 | -1.8947
|  | W/m2 | 冷房顕熱 | 47.6 | 23.8 |  | 60.49 | 59.46 | 38.7301 | 83.2209
|  |  | 冷房潜熱 | 15.8 | 8.8 |  | 18.39 | 24.6 | 32.2121 | 47.197 |  |  |  | 図9 1F中央監視室（積算負荷） | 図10 1F中央監視室（最大負荷）
|  |  | 暖房顕熱 | -155.1 | -92.4 |  | -134.7 | -140.24 | -162.5551 | -211.0481
|  |  | 暖房潜熱 | -6.7 | -5.4 |  | -10.57 | -14.22 | -27.6659 | -86.9129
----1F_事務室1----
1F事務室1 | 積算負荷 | MWh | 冷房顕熱 | 15.662 | 15.4108 |  | 18.3831 | 13.7848 | 14.7659 | 14.8135
|  |  | 冷房潜熱 | 5.3889 | 5.4744 |  | 4.4014 | 7.3236 | 4.0231 | 5.0236
|  |  | 暖房顕熱 | -16.1728 | -21.9846 |  | -9.6508 | -22.3787 | -15.1642 | -16.5046
|  |  | 暖房潜熱 | -0.19939 | -0.46408 |  | -0.56023 | -4.2778 | -0.33476 | -1.879
|  | MJ/m2年 | 冷房顕熱 | 153.716 | 151.2515 |  | 180.4232 | 135.2928 | 144.922 | 145.3883
|  |  | 冷房潜熱 | 52.8898 | 53.7289 |  | 43.1985 | 71.878 | 39.485 | 49.3046
|  |  | 暖房顕熱 | -158.7298 | -215.7707 |  | -94.7187 | -219.6386 | -148.8311 | -161.9859
|  |  | 暖房潜熱 | -1.957 | -4.5547 |  | -5.4985 | -41.985 | -3.2855 | -18.4414
| 最大負荷 | kW | 冷房顕熱 | 32.2784 | 49.2612 |  | 35.3118 | 39.508 | 50.1815 | 27.7374
|  |  | 冷房潜熱 | 7.4094 | 12.2511 |  | 17.7568 | 27.1982 | 13.2786 | 18.6224
|  |  | 暖房顕熱 | -78.3852 | -124.5286 |  | -46.1068 | -87.1333 | -91.1639 | -42.783
|  |  | 暖房潜熱 | -1.724 | -5.6487 |  | -8.5281 | -13.0617 | -8.7889 | -29.2452
|  | W/m2 | 冷房顕熱 | 88 | 134.3 |  | 96.27 | 107.71 | 136.8088 | 75.6199 |  |  |  | 図11 1F更衣室1（積算負荷） | 図12 1F更衣室1（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 33.4 |  | 48.41 | 74.15 | 36.2012 | 50.7699
|  |  | 暖房顕熱 | -213.7 | -339.5 |  | -125.7 | -237.55 | -248.5385 | -116.6385
|  |  | 暖房潜熱 | -4.7 | -15.4 |  | -23.25 | -35.61 | -23.9611 | -79.7307
----1F_事務室2----
1F事務室2 | 積算負荷 | MWh | 冷房顕熱 | 13.4816 | 12.6419 |  | 16.2686 | 11.7588 | 12.1601 | 12.8244
|  |  | 冷房潜熱 | 4.0108 | 4.0744 |  | 3.3216 | 5.4122 | 2.9943 | 3.3386
|  |  | 暖房顕熱 | -9.3961 | -17.7285 |  | -4.4957 | -13.06 | -8.0385 | -9.6786
|  |  | 暖房潜熱 | -0.1484 | -0.3454 |  | -0.40761 | -3.0974 | -0.24915 | -0.51276
|  | MJ/m2年 | 冷房顕熱 | 177.7795 | 166.7063 |  | 214.5309 | 155.0613 | 160.3524 | 169.1132
|  |  | 冷房潜熱 | 52.8898 | 53.7289 |  | 43.8012 | 71.3696 | 39.485 | 44.0249
|  |  | 暖房顕熱 | -123.9044 | -233.7826 |  | -59.2845 | -172.2204 | -106.0019 | -127.6293
|  |  | 暖房潜熱 | -1.957 | -4.5547 |  | -5.3751 | -40.8443 | -3.2855 | -6.7616
| 最大負荷 | kW | 冷房顕熱 | 26.5356 | 51.6789 |  | 26.9587 | 30.7971 | 36.4295 | 19.2412
|  |  | 冷房潜熱 | 5.5146 | 9.1182 |  | 13.2269 | 20.2784 | 9.8829 | 14.4493
|  |  | 暖房顕熱 | -60.3057 | -130.4667 |  | -30.0409 | -59.5386 | -61.3081 | -31.6548
|  |  | 暖房潜熱 | -1.2831 | -2.7573 |  | -4.1059 | -7.8815 | -6.5414 | -20.0879
|  | W/m2 | 冷房顕熱 | 97.2 | 189.3 |  | 98.75 | 112.81 | 133.4415 | 70.4805 |  |  |  | 図13 1F更衣室2（積算負荷） | 図14 1F更衣室2（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 33.4 |  | 48.45 | 74.28 | 36.2012 | 52.9278
|  |  | 暖房顕熱 | -220.9 | -477.9 |  | -110.04 | -218.09 | -224.5719 | -115.9518
|  |  | 暖房潜熱 | -4.7 | -10.1 |  | -15.04 | -28.87 | -23.9611 | -73.5821
----2-6F_廊下----
2-6F廊下 | 積算負荷 | MWh | 冷房顕熱 | 10.8231 | 3.9572 |  | 13.6554 | 12.2173 | 13.3261 | 31.1199
|  |  | 冷房潜熱 | 1.114 | 0.026482 |  | 1.1646 | 1.1751 | 1.4946 | 2.177
|  |  | 暖房顕熱 | -21.0157 | -0.32829 |  | -21.2096 | -18.9069 | -36.5022 | -0.75542
|  |  | 暖房潜熱 | -1.4098 | -0.032227 |  | -1.357 | -1.3912 | -1.7408 | -1.682
|  | MJ/m2年 | 冷房顕熱 | 54.1156 | 19.7861 |  | 68.2768 | 61.0864 | 66.6304 | 155.5996
|  |  | 冷房潜熱 | 5.5699 | 0.13241 |  | 5.8229 | 5.8756 | 7.473 | 10.885
|  |  | 暖房顕熱 | -105.0786 | -1.6415 |  | -106.048 | -94.5347 | -182.5112 | -3.7771
|  |  | 暖房潜熱 | -7.0488 | -0.16114 |  | -6.785 | -6.9558 | -8.7041 | -8.4101
| 最大負荷 | kW | 冷房顕熱 | 26.712 | 2.6928 |  | 36.1152 | 33.0048 | 29.6514 | 36.4516
|  |  | 冷房潜熱 | 10.512 | 0.9792 |  | 12.2256 | 16.3512 | 18.3398 | 13.6272
|  |  | 暖房顕熱 | -74.736 | -3.1824 |  | -70.0056 | -63.0576 | -112.2064 | -5.6046
|  |  | 暖房潜熱 | -4.464 | -1.584 |  | -4.9896 | -6.3432 | -15.7515 | -25.1668
|  | W/m2 | 冷房顕熱 | 37.1 | 3.74 |  | 50.16 | 45.84 | 41.1825 | 50.6273 |  |  |  | 図15 1F休憩室（積算負荷） | 図16 1F休憩室（最大負荷）
|  |  | 冷房潜熱 | 14.6 | 1.36 |  | 16.98 | 22.71 | 25.472 | 18.9267
|  |  | 暖房顕熱 | -103.8 | -4.42 |  | -97.23 | -87.58 | -155.8422 | -7.7842
|  |  | 暖房潜熱 | -6.2 | -2.2 |  | -6.93 | -8.81 | -21.877 | -34.9539
----2-6F_自販機コーナー----
2-6F自販機ｺｰﾅｰ | 積算負荷 | MWh | 冷房顕熱 | 1.7892 | 0.50095 |  | 2.3395 | 2.0807 | 2.2416 | 3.7877
|  |  | 冷房潜熱 | 0.18232 | 0.029919 |  | 0.19126 | 0.1902 | 0.22627 | 0.40807
|  |  | 暖房顕熱 | -4.0841 | -0.37183 |  | -3.9933 | -3.6471 | -5.1354 | -0.7142
|  |  | 暖房潜熱 | -0.23099 | -0.037538 |  | -0.22265 | -0.22575 | -0.26354 | -0.432
|  | MJ/m2年 | 冷房顕熱 | 59.1602 | 16.5642 |  | 77.2683 | 68.7212 | 74.1195 | 125.098
|  |  | 冷房潜熱 | 6.0286 | 0.98928 |  | 6.3168 | 6.282 | 7.4816 | 13.4775
|  |  | 暖房顕熱 | -135.0414 | -12.2948 |  | -131.8893 | -120.4563 | -169.8045 | -23.5883
|  |  | 暖房潜熱 | -7.6378 | -1.2412 |  | -7.3534 | -7.456 | -8.714 | -14.2679
| 最大負荷 | kW | 冷房顕熱 | 4.7905 | 1.1541 |  | 6.2599 | 5.7323 | 4.6128 | 6.1043
|  |  | 冷房潜熱 | 1.7202 | 0.07839 |  | 2.0045 | 2.6814 | 2.7764 | 4.4451
|  |  | 暖房顕熱 | -13.4243 | -0.87971 |  | -12.3072 | -11.3676 | -16.174 | -7.5554
|  |  | 暖房潜熱 | -0.72946 | -0.27872 |  | -0.8175 | -1.0399 | -2.3846 | -5.4424
|  | W/m2 | 冷房顕熱 | 44 | 10.6 |  | 57.43 | 52.59 | 42.3674 | 56.0028 |  |  |  | 図17 1F自販機ｺｰﾅｰ（積算負荷） | 図18 1F自販機ｺｰﾅｰ（最大負荷）
|  |  | 冷房潜熱 | 15.8 | 0.72 |  | 18.39 | 24.6 | 25.5012 | 40.7804
|  |  | 暖房顕熱 | -123.3 | -8.08 |  | -112.91 | -104.29 | -148.5556 | -69.3157
|  |  | 暖房潜熱 | -6.7 | -2.56 |  | -7.5 | -9.54 | -21.9021 | -49.9303
----2-6F_EVホール----
2-6FEVホール | 積算負荷 | MWh | 冷房顕熱 | 0.93766 | 0.25114 |  | 0.22209 | 1.1049 | 1.2388 | 3.2004
|  |  | 冷房潜熱 | 0.10048 | 0.0022044 |  | 0.021056 | 0.1002 | 0.12455 | 0.22395
|  |  | 暖房顕熱 | -4.0921 | -0.16364 |  | -0.85823 | -3.7541 | -4.1444 | -0.056742
|  |  | 暖房潜熱 | -0.1273 | -0.0026796 |  | -0.024511 | -0.11981 | -0.14507 | -0.20875
|  | MJ/m2年 | 冷房顕熱 | 56.2597 | 15.0682 |  | 66.6273 | 66.2941 | 74.3309 | 192.0217
|  |  | 冷房潜熱 | 6.0286 | 0.13226 |  | 6.3168 | 6.0118 | 7.473 | 13.4367
|  |  | 暖房顕熱 | -245.5261 | -9.8184 |  | -257.4704 | -225.2446 | -248.6646 | -3.4045
|  |  | 暖房潜熱 | -7.6378 | -0.16078 |  | -7.3534 | -7.1884 | -8.7041 | -12.5252
| 最大負荷 | kW | 冷房顕熱 | 3.09 | 0.2424 |  | 0.79296 | 3.723 | 3.0028 | 3.6964
|  |  | 冷房潜熱 | 0.948 | 0.0816 |  | 0.22068 | 1.476 | 1.5283 | 1.438
|  |  | 暖房顕熱 | -9.516 | -0.402 |  | -1.8406 | -8.3136 | -11.412 | -0.31229
|  |  | 暖房潜熱 | -0.402 | -0.132 |  | -0.09 | -0.5724 | -1.3126 | -3.0113
|  | W/m2 | 冷房顕熱 | 51.5 | 4.04 |  | 66.08 | 62.05 | 50.0469 | 61.6074 |  |  |  | 図19 1F事務室1（積算負荷） | 図20 1F事務室1（最大負荷）
|  |  | 冷房潜熱 | 15.8 | 1.36 |  | 18.39 | 24.6 | 25.472 | 23.9668
|  |  | 暖房顕熱 | -158.6 | -6.7 |  | -153.38 | -138.56 | -190.2004 | -5.2048
|  |  | 暖房潜熱 | -6.7 | -2.2 |  | -7.5 | -9.54 | -21.877 | -50.1876
----2-6F_事務室1_ペリメータ北----
2-6F事務室1NP | 積算負荷 | MWh | 冷房顕熱 | 54.0787 | 64.5894 |  | 66.8002 | 52.9349 | 59.3367 | 66.3584
|  |  | 冷房潜熱 | 13.7734 | 13.6177 |  | 11.3994 | 10.442 | 10.0822 | 11.7203
|  |  | 暖房顕熱 | -17.3949 | -17.4969 |  | -10.4849 | -11.621 | -13.1153 | -5.0537
|  |  | 暖房潜熱 | -0.50962 | -0.34041 |  | -0.96352 | 0.056222 | -0.57375 | -2.9488
|  | MJ/m2年 | 冷房顕熱 | 207.6624 | 248.0234 |  | 256.5129 | 203.27 | 227.8527 | 254.8162
|  |  | 冷房潜熱 | 52.8898 | 52.2918 |  | 43.7737 | 40.0971 | 38.7157 | 45.0058
|  |  | 暖房顕熱 | -66.7966 | -67.1882 |  | -40.2618 | -44.6247 | -50.3626 | -19.4063
|  |  | 暖房潜熱 | -1.957 | -1.3072 |  | -3.6999 | 0.21589 | -2.2032 | -11.3233
| 最大負荷 | kW | 冷房顕熱 | 88.9688 | 198.0938 |  | 96.8625 | 100.1531 | 135.2971 | 56.4175
|  |  | 冷房潜熱 | 18.9375 | 22.2188 |  | 39.0281 | 38.9906 | 27.6493 | 32.1133
|  |  | 暖房顕熱 | -133.7812 | -219.6562 |  | -74.8875 | -103.1156 | -157.0319 | -46.7582
|  |  | 暖房潜熱 | -4.4062 | -9.5625 |  | -16.7625 | -17.2688 | -17.0024 | -47.5584
|  | W/m2 | 冷房顕熱 | 94.9 | 211.3 |  | 103.32 | 106.83 | 144.3169 | 60.1786 |  |  |  | 図21 1F事務室2（積算負荷） | 図22 1F事務室2（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 23.7 |  | 41.63 | 41.59 | 29.4926 | 34.2542
|  |  | 暖房顕熱 | -142.7 | -234.3 |  | -79.88 | -109.99 | -167.5007 | -49.8754
|  |  | 暖房潜熱 | -4.7 | -10.2 |  | -17.88 | -18.42 | -18.1359 | -50.7289
----2-6F_事務室1_ペリメータ北東----
2-6F事務室1NEP | 積算負荷 | MWh | 冷房顕熱 | 18.7306 | 21.9418 |  | 23.547 | 17.7709 | 19.8536 | 24.1418
|  |  | 冷房潜熱 | 4.2238 | 4.1761 |  | 3.5362 | 3.0317 | 3.0919 | 3.8533
|  |  | 暖房顕熱 | -3.9823 | -2.8027 |  | -3.009 | -4.8867 | -3.5946 | -1.1772
|  |  | 暖房潜熱 | -0.15629 | -0.10456 |  | -0.28962 | 0.18705 | -0.17595 | -0.82903
|  | MJ/m2年 | 冷房顕熱 | 234.5396 | 274.7498 |  | 294.8489 | 222.5224 | 248.6019 | 302.2975
|  |  | 冷房潜熱 | 52.8898 | 52.2925 |  | 44.2794 | 37.962 | 38.7157 | 48.2495
|  |  | 暖房顕熱 | -49.8654 | -35.0946 |  | -37.6775 | -61.1896 | -45.0107 | -14.74
|  |  | 暖房潜熱 | -1.957 | -1.3093 |  | -3.6265 | 2.3422 | -2.2032 | -10.3809
| 最大負荷 | kW | 冷房顕熱 | 31.3663 | 44.045 |  | 40.5231 | 39.8475 | 44.3486 | 19.3274
|  |  | 冷房潜熱 | 5.8075 | 6.8137 |  | 11.5 | 12.0549 | 8.4791 | 12.2593
|  |  | 暖房顕熱 | -35.995 | -35.0463 |  | -20.6482 | -31.3864 | -46.9809 | -19.9188
|  |  | 暖房潜熱 | -1.3513 | -2.9325 |  | -3.3062 | -5.3187 | -5.2141 | -16.7777
|  | W/m2 | 冷房顕熱 | 109.1 | 153.2 |  | 140.95 | 138.6 | 154.2562 | 67.2257 |  |  |  | 図23 2-6F廊下（積算負荷） | 図24 2-6F廊下（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 23.7 |  | 40 | 41.93 | 29.4926 | 42.6409
|  |  | 暖房顕熱 | -125.2 | -121.9 |  | -71.82 | -109.17 | -163.4119 | -69.2827
|  |  | 暖房潜熱 | -4.7 | -10.2 |  | -11.5 | -18.5 | -18.1359 | -58.3573
----2-6F_事務室1_ペリメータ北西----
2-6F事務室1NWP | 積算負荷 | MWh | 冷房顕熱 | 19.2411 | 22.2494 |  | 23.915 | 19.776 | 19.7483 | 22.3546
|  |  | 冷房潜熱 | 4.2238 | 4.1761 |  | 3.5017 | 3.1721 | 3.0919 | 3.8077
|  |  | 暖房顕熱 | -4.7862 | -3.5408 |  | -3.9007 | -4.2363 | -4.079 | -1.734
|  |  | 暖房潜熱 | -0.15629 | -0.10456 |  | -0.29658 | 0.054616 | -0.17595 | -0.97722
|  | MJ/m2年 | 冷房顕熱 | 240.9322 | 278.6011 |  | 299.4573 | 247.6301 | 247.2829 | 279.9184
|  |  | 冷房潜熱 | 52.8898 | 52.2925 |  | 43.848 | 39.7208 | 38.7157 | 47.6793
|  |  | 暖房顕熱 | -59.931 | -44.3372 |  | -48.8438 | -53.0458 | -51.0761 | -21.7129
|  |  | 暖房潜熱 | -1.957 | -1.3093 |  | -3.7138 | 0.68389 | -2.2032 | -12.2365
| 最大負荷 | kW | 冷房顕熱 | 26.565 | 38.0938 |  | 31.3203 | 32.2 | 42.7225 | 17.5563
|  |  | 冷房潜熱 | 5.8075 | 6.8137 |  | 11.9772 | 11.9686 | 8.4791 | 11.6648
|  |  | 暖房顕熱 | -37.95 | -38.3525 |  | -26.5132 | -33.3184 | -50.3181 | -20.3893
|  |  | 暖房潜熱 | -1.3513 | -2.9325 |  | -3.2976 | -5.3015 | -5.2141 | -16.0853
|  | W/m2 | 冷房顕熱 | 92.4 | 132.5 |  | 108.94 | 112 | 148.6001 | 61.0655 |  |  |  | 図25 2-6F自販機ｺｰﾅｰ（積算負荷） | 図26 2-6F自販機ｺｰﾅｰ（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 23.7 |  | 41.66 | 41.63 | 29.4926 | 40.5731
|  |  | 暖房顕熱 | -132 | -133.4 |  | -92.22 | -115.89 | -175.0195 | -70.9193
|  |  | 暖房潜熱 | -4.7 | -10.2 |  | -11.47 | -18.44 | -18.1359 | -55.949
----2-6F_事務室1_インテリア----
2-6F事務室1NI | 積算負荷 | MWh | 冷房顕熱 | 96.7691 | 119.0833 |  | 101.2727 | 88.4682 | 93.05 | 111.2192
|  |  | 冷房潜熱 | 21.4865 | 21.5853 |  | 17.8404 | 17.3372 | 15.7282 | 18.1985
|  |  | 暖房顕熱 | -4.4089 | -0.79238 |  | -2.6095 | -4.328 | -7.735 | 0
|  |  | 暖房潜熱 | -0.79502 | -0.33813 |  | -1.4629 | -0.70187 | -0.89505 | -2.58
|  | MJ/m2年 | 冷房顕熱 | 238.2008 | 293.1282 |  | 249.2867 | 217.768 | 229.0461 | 273.7702
|  |  | 冷房潜熱 | 52.8898 | 53.1331 |  | 43.9149 | 42.6763 | 38.7157 | 44.7964
|  |  | 暖房顕熱 | -10.8526 | -1.9505 |  | -6.4234 | -10.6536 | -19.0399 | 0
|  |  | 暖房潜熱 | -1.957 | -0.83232 |  | -3.601 | -1.7277 | -2.2032 | -6.3507
| 最大負荷 | kW | 冷房顕熱 | 105.1538 | 106.6163 |  | 120.2175 | 131.3618 | 186.453 | 83.5743
|  |  | 冷房潜熱 | 29.5425 | 32.0287 |  | 60.3135 | 60.5036 | 43.1329 | 39.9531
|  |  | 暖房顕熱 | -146.3963 | -69.4688 |  | -80.3351 | -134.3014 | -208.783 | 0
|  |  | 暖房潜熱 | -6.8738 | -13.455 |  | -25.4768 | -16.5409 | -26.5237 | -53.4538
|  | W/m2 | 冷房顕熱 | 71.9 | 72.9 |  | 82.2 | 89.82 | 127.4893 | 57.1448 |  |  |  | 図27 2-6FEVホール（積算負荷） | 図28 2-6FEVホール（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 21.9 |  | 41.24 | 41.37 | 29.4926 | 27.3184
|  |  | 暖房顕熱 | -100.1 | -47.5 |  | -54.93 | -91.83 | -142.7576 | 0
|  |  | 暖房潜熱 | -4.7 | -9.2 |  | -17.42 | -11.31 | -18.1359 | -36.5496
----2-6F_事務室2_ペリメータ南----
2-6F事務室2SP | 積算負荷 | MWh | 冷房顕熱 | 70.7473 | 83.0447 |  | 86.5992 | 72.2017 | 56.6618 | 82.1078
|  |  | 冷房潜熱 | 12.3042 | 12.1443 |  | 10.4371 | 10.0593 | 9.0068 | 10.9017
|  |  | 暖房顕熱 | -4.48 | -4.4487 |  | -3.6415 | -3.6745 | -9.5904 | -1.2007
|  |  | 暖房潜熱 | -0.45526 | -0.27277 |  | -0.84268 | -0.41688 | -0.51255 | -2.0142
|  | MJ/m2年 | 冷房顕熱 | 304.1078 | 356.9681 |  | 372.2474 | 310.3597 | 243.5614 | 352.9411
|  |  | 冷房潜熱 | 52.8898 | 52.2025 |  | 44.8641 | 43.2398 | 38.7157 | 46.8609
|  |  | 暖房顕熱 | -19.2571 | -19.1228 |  | -15.6531 | -15.7949 | -41.2246 | -5.161
|  |  | 暖房潜熱 | -1.957 | -1.1725 |  | -3.6223 | -1.792 | -2.2032 | -8.6581
| 最大負荷 | kW | 冷房顕熱 | 74.705 | 153.1788 |  | 83.1805 | 86.8655 | 111.1584 | 50.3686
|  |  | 冷房潜熱 | 16.9175 | 19.43 |  | 34.572 | 34.6558 | 24.7 | 29.142
|  |  | 暖房顕熱 | -89.11 | -81.8238 |  | -45.1831 | -68.7839 | -129.3054 | -40.5462
|  |  | 暖房潜熱 | -3.9362 | -12.3113 |  | -9.1539 | -9.3381 | -15.1888 | -45.1201
|  | W/m2 | 冷房顕熱 | 89.2 | 182.9 |  | 99.32 | 103.72 | 132.7264 | 60.1416 |  |  |  | 図29 2-6F事務室1NP（積算負荷） | 図30 2-6F事務室1NP（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 23.2 |  | 41.28 | 41.38 | 29.4926 | 34.7964
|  |  | 暖房顕熱 | -106.4 | -97.7 |  | -53.95 | -82.13 | -154.3946 | -48.4134
|  |  | 暖房潜熱 | -4.7 | -14.7 |  | -10.93 | -11.15 | -18.1359 | -53.8747
----2-6F_事務室2_ペリメータ南西----
2-6F事務室2SWP | 積算負荷 | MWh | 冷房顕熱 | 19.655 | 23.0681 |  | 24.4078 | 20.2312 | 19.8317 | 24.0261
|  |  | 冷房潜熱 | 4.2238 | 4.169 |  | 3.5132 | 3.2167 | 3.0919 | 3.8132
|  |  | 暖房顕熱 | -4.0394 | -3.3097 |  | -3.1333 | -3.4353 | -2.8091 | -0.93783
|  |  | 暖房潜熱 | -0.15629 | -0.093955 |  | -0.29232 | 0.027692 | -0.17595 | -0.79603
|  | MJ/m2年 | 冷房顕熱 | 246.1147 | 288.8525 |  | 305.6281 | 253.3298 | 248.3271 | 300.8484
|  |  | 冷房潜熱 | 52.8898 | 52.2032 |  | 43.9908 | 40.2783 | 38.7157 | 47.7482
|  |  | 暖房顕熱 | -50.5804 | -41.4432 |  | -39.2344 | -43.0154 | -35.1743 | -11.7432
|  |  | 暖房潜熱 | -1.957 | -1.1765 |  | -3.6603 | 0.34675 | -2.2032 | -9.9677
| 最大負荷 | kW | 冷房顕熱 | 26.105 | 51.0025 |  | 30.2824 | 31.3835 | 38.2279 | 17.1677
|  |  | 冷房潜熱 | 5.8075 | 6.67 |  | 11.9054 | 11.9226 | 8.4791 | 11.8519
|  |  | 暖房顕熱 | -32.6887 | -35.4487 |  | -23.0805 | -31.0356 | -47.0994 | -20.1966
|  |  | 暖房潜熱 | -1.3513 | -1.725 |  | -3.174 | -3.2315 | -5.2141 | -16.2693
|  | W/m2 | 冷房顕熱 | 90.8 | 177.4 |  | 105.33 | 109.16 | 132.9667 | 59.7138 |  |  |  | 図31 2-6F事務室1NEP（積算負荷） | 図32 2-6F事務室1NEP（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 23.2 |  | 41.41 | 41.47 | 29.4926 | 41.224
|  |  | 暖房顕熱 | -113.7 | -123.3 |  | -80.28 | -107.95 | -163.8241 | -70.2491
|  |  | 暖房潜熱 | -4.7 | -6 |  | -11.04 | -11.24 | -18.1359 | -56.5888
----2-6F_事務室2_インテリア----
2-6F事務室2SI | 積算負荷 | MWh | 冷房顕熱 | 102.4594 | 127.9903 |  | 104.9878 | 92.7298 | 96.6097 | 117.6801
|  |  | 冷房潜熱 | 20.4948 | 20.5587 |  | 17.1038 | 16.6474 | 15.0023 | 16.9596
|  |  | 暖房顕熱 | -1.7966 | -0.33201 |  | -0.86604 | -1.6532 | -5.6708 | 0
|  |  | 暖房潜熱 | -0.75832 | -0.27816 |  | -1.3686 | -0.63745 | -0.85374 | -2.5226
|  | MJ/m2年 | 冷房顕熱 | 264.4114 | 330.2975 |  | 270.9363 | 239.3026 | 249.3152 | 303.6905
|  |  | 冷房潜熱 | 52.8898 | 53.0546 |  | 44.1389 | 42.9611 | 38.7157 | 43.7667
|  |  | 暖房顕熱 | -4.6364 | -0.8568 |  | -2.235 | -4.2664 | -14.6344 | 0
|  |  | 暖房潜熱 | -1.957 | -0.71784 |  | -3.5318 | -1.645 | -2.2032 | -6.5099
| 最大負荷 | kW | 冷房顕熱 | 100.8585 | 208.134 |  | 109.1727 | 121.2116 | 165.2842 | 80.7453
|  |  | 冷房潜熱 | 28.179 | 17.019 |  | 57.0416 | 57.3903 | 41.1422 | 37.9462
|  |  | 暖房顕熱 | -119.133 | -61.5195 |  | -69.9871 | -109.2006 | -193.7385 | 0
|  |  | 暖房潜熱 | -6.5565 | -18.135 |  | -14.6754 | -15.1079 | -25.2995 | -48.8742
|  | W/m2 | 冷房顕熱 | 72.3 | 149.2 |  | 78.26 | 86.89 | 118.4833 | 57.8819 |  |  |  | 図33 2-6F事務室1NWP（積算負荷） | 図34 2-6F事務室1NWP（最大負荷）
|  |  | 冷房潜熱 | 20.2 | 12.2 |  | 40.89 | 41.14 | 29.4926 | 27.2016
|  |  | 暖房顕熱 | -85.4 | -44.1 |  | -50.17 | -78.28 | -138.8806 | 0
|  |  | 暖房潜熱 | -4.7 | -13 |  | -10.52 | -10.83 | -18.1359 | -35.0353
----7F_廊下----
7F廊下 | 積算負荷 | MWh | 冷房顕熱 | 2.5653 | 3.5772 |  | 2.718 | 2.6608 | 3.2525 | 4.7131
|  |  | 冷房潜熱 | 0.2228 | 0.026482 |  | 0.23292 | 0.23652 | 0.29892 | 0.58972
|  |  | 暖房顕熱 | -6.4602 | -2.3612 |  | -5.9528 | -6.0169 | -8.3097 | -2.4518
|  |  | 暖房潜熱 | -0.28195 | -0.032227 |  | -0.2714 | -0.27979 | -0.34816 | -0.59769
|  | MJ/m2年 | 冷房顕熱 | 64.1315 | 89.4301 |  | 67.9489 | 66.5206 | 81.3122 | 117.8287
|  |  | 冷房潜熱 | 5.5699 | 0.66204 |  | 5.8229 | 5.9129 | 7.473 | 14.743
|  |  | 暖房顕熱 | -161.5054 | -59.0306 |  | -148.8192 | -150.422 | -207.7427 | -61.2959
|  |  | 暖房潜熱 | -7.0488 | -0.80568 |  | -6.785 | -6.9949 | -8.7041 | -14.9423
| 最大負荷 | kW | 冷房顕熱 | 7.632 | 3.3552 |  | 7.547 | 7.3699 | 7.6413 | 10.1669
|  |  | 冷房潜熱 | 2.1024 | 1.0944 |  | 2.4451 | 3.2702 | 3.668 | 4.3337
|  |  | 暖房顕熱 | -18.2736 | -6.3072 |  | -14.5282 | -14.9731 | -22.2565 | -8.7584
|  |  | 暖房潜熱 | -0.8928 | -0.8784 |  | -1.3954 | -1.9224 | -3.1503 | -7.2816
|  | W/m2 | 冷房顕熱 | 53 | 23.3 |  | 52.41 | 51.18 | 53.0644 | 70.6034 |  |  |  | 図35 2-6F事務室1NI（積算負荷） | 図36 2-6F事務室1NI（最大負荷）
|  |  | 冷房潜熱 | 14.6 | 7.6 |  | 16.98 | 22.71 | 25.472 | 30.0954
|  |  | 暖房顕熱 | -126.9 | -43.8 |  | -100.89 | -103.98 | -154.5591 | -60.822
|  |  | 暖房潜熱 | -6.2 | -6.1 |  | -9.69 | -13.35 | -21.877 | -50.5667
----7F_自販機コーナー----
7F自販機ｺｰﾅｰ | 積算負荷 | MWh | 冷房顕熱 | 0.42453 | 0.53868 |  | 0.46659 | 0.44905 | 0.57833 | 0.71673
|  |  | 冷房潜熱 | 0.036464 | 0.029919 |  | 0.038252 | 0.038164 | 0.045253 | 0.10247
|  |  | 暖房顕熱 | -1.161 | -0.74431 |  | -1.0561 | -1.071 | -1.1785 | -0.75971
|  |  | 暖房潜熱 | -0.046198 | -0.037538 |  | -0.044529 | -0.045264 | -0.052708 | -0.12688
|  | MJ/m2年 | 冷房顕熱 | 70.1867 | 89.059 |  | 77.0521 | 74.1555 | 95.6131 | 118.3588
|  |  | 冷房潜熱 | 6.0286 | 4.9464 |  | 6.3168 | 6.3023 | 7.4816 | 16.9213
|  |  | 暖房顕熱 | -191.943 | -123.0552 |  | -174.3941 | -176.8645 | -194.8443 | -125.4563
|  |  | 暖房潜熱 | -7.6378 | -6.206 |  | -7.3534 | -7.4747 | -8.714 | -20.9521
| 最大負荷 | kW | 冷房顕熱 | 1.3326 | 0.60099 |  | 1.2877 | 1.2437 | 1.205 | 1.9197
|  |  | 冷房潜熱 | 0.34404 | 0.25041 |  | 0.4009 | 0.53628 | 0.55529 | 0.90999
|  |  | 暖房顕熱 | -3.2249 | -1.4459 |  | -2.5563 | -2.599 | -3.2185 | -2.7718
|  |  | 暖房潜熱 | -0.14589 | -0.15678 |  | -0.2289 | -0.31545 | -0.47692 | -1.3749
|  | W/m2 | 冷房顕熱 | 61.2 | 27.6 |  | 59.07 | 57.05 | 55.3384 | 88.0607 |  |  |  | 図37 2-6F事務室2SP（積算負荷） | 図38 2-6F事務室2SP（最大負荷）
|  |  | 冷房潜熱 | 15.8 | 11.5 |  | 18.39 | 24.6 | 25.5012 | 41.7425
|  |  | 暖房顕熱 | -148.1 | -66.4 |  | -117.26 | -119.22 | -147.8079 | -127.1488
|  |  | 暖房潜熱 | -6.7 | -7.2 |  | -10.5 | -14.47 | -21.9021 | -63.0674
----7F_EVホール----
7FEVホール | 積算負荷 | MWh | 冷房顕熱 | 0.22694 | 0.27276 |  | 0.23563 | 0.23508 | 0.30147 | 0.48725
|  |  | 冷房潜熱 | 0.020095 | 0.0022044 |  | 0.021056 | 0.020274 | 0.02491 | 0.070379
|  |  | 暖房顕熱 | -1.0007 | -0.39328 |  | -0.99385 | -0.96387 | -0.93193 | -0.35928
|  |  | 暖房潜熱 | -0.025459 | -0.0026796 |  | -0.024511 | -0.024182 | -0.029014 | -0.084688
|  | MJ/m2年 | 冷房顕熱 | 68.0828 | 81.8273 |  | 70.6884 | 70.5231 | 90.4407 | 146.1764
|  |  | 冷房潜熱 | 6.0286 | 0.66132 |  | 6.3168 | 6.0821 | 7.473 | 21.1138
|  |  | 暖房顕熱 | -300.2022 | -117.9839 |  | -298.1544 | -289.1599 | -279.5802 | -107.7839
|  |  | 暖房潜熱 | -7.6378 | -0.80388 |  | -7.3534 | -7.2545 | -8.7041 | -25.4064
| 最大負荷 | kW | 冷房顕熱 | 0.828 | 0.3216 |  | 0.83232 | 0.80364 | 0.76094 | 1.1745
|  |  | 冷房潜熱 | 0.1896 | 0.0912 |  | 0.22068 | 0.2952 | 0.30566 | 0.49822
|  |  | 暖房顕熱 | -2.2008 | -0.6972 |  | -1.9182 | -1.8875 | -2.267 | -0.99547
|  |  | 暖房潜熱 | -0.0804 | -0.072 |  | -0.12048 | -0.17364 | -0.26252 | -0.91179
|  | W/m2 | 冷房顕熱 | 69 | 26.8 |  | 69.36 | 66.97 | 63.4118 | 97.8752 |  |  |  | 図39 2-6F事務室2SWP（積算負荷） | 図40 2-6F事務室2SWP（最大負荷）
|  |  | 冷房潜熱 | 15.8 | 7.6 |  | 18.39 | 24.6 | 25.472 | 41.5187
|  |  | 暖房顕熱 | -183.4 | -58.1 |  | -159.85 | -157.29 | -188.9176 | -82.9556
|  |  | 暖房潜熱 | -6.7 | -6 |  | -10.04 | -14.47 | -21.877 | -75.9827
----7F_事務室1----
7F事務室1 | 積算負荷 | MWh | 冷房顕熱 | 33.3652 | 35.7157 |  | 36.6551 | 30.348 | 35.545 | 35.6435
|  |  | 冷房潜熱 | 8.7415 | 8.8903 |  | 7.0069 | 6.1635 | 6.3988 | 7.802
|  |  | 暖房顕熱 | -13.44 | -12.4532 |  | -7.3631 | -12.5111 | -11.1325 | -8.4927
|  |  | 暖房潜熱 | -0.32344 | -0.96009 |  | -0.63811 | 0.38013 | -0.36414 | -2.1726
|  | MJ/m2年 | 冷房顕熱 | 201.8736 | 216.095 |  | 221.7789 | 183.6183 | 215.0623 | 215.6581
|  |  | 冷房潜熱 | 52.8898 | 53.7901 |  | 42.3948 | 37.2917 | 38.7157 | 47.2053
|  |  | 暖房顕熱 | -81.3175 | -75.3473 |  | -44.5501 | -75.6977 | -67.3566 | -51.3847
|  |  | 暖房潜熱 | -1.957 | -5.809 |  | -3.8609 | 2.2999 | -2.2032 | -13.1452
| 最大負荷 | kW | 冷房顕熱 | 64.6765 | 99.603 |  | 55.4838 | 63.4687 | 83.348 | 44.6082
|  |  | 冷房潜熱 | 12.019 | 18.3855 |  | 24.7937 | 25.2339 | 17.5481 | 25.1093
|  |  | 暖房顕熱 | -100.674 | -143.99 |  | -51.3545 | -85.7752 | -98.1778 | -36.0315
|  |  | 暖房潜熱 | -2.7965 | -7.9135 |  | -11.1741 | -11.9 | -10.7908 | -37.9023 |  |  |  | 図41 2-6F事務室2SI（積算負荷） | 図42 2-6F事務室2SI（最大負荷）
|  | W/m2 | 冷房顕熱 | 108.7 | 167.4 |  | 93.25 | 106.67 | 140.0806 | 74.9718
|  |  | 冷房潜熱 | 20.2 | 30.9 |  | 41.67 | 42.41 | 29.4926 | 42.2004
|  |  | 暖房顕熱 | -169.2 | -242 |  | -86.31 | -144.16 | -165.0048 | -60.5571
|  |  | 暖房潜熱 | -4.7 | -13.3 |  | -18.78 | -20 | -18.1359 | -63.7013
----7F_事務室2----
7F事務室2 | 積算負荷 | MWh | 冷房顕熱 | 32.0977 | 36.9832 |  | 35.9202 | 29.2604 | 31.7938 | 34.4748
|  |  | 冷房潜熱 | 7.4046 | 7.4606 |  | 5.9963 | 5.6484 | 5.4202 | 6.5707
|  |  | 暖房顕熱 | -6.3151 | -6.034 |  | -3.2842 | -6.1199 | -6.3555 | -4.4265
|  |  | 暖房潜熱 | -0.27397 | -0.55778 |  | -0.52677 | -0.025971 | -0.30845 | -1.5781
|  | MJ/m2年 | 冷房顕熱 | 229.2696 | 264.1655 |  | 256.5725 | 209.003 | 227.0984 | 246.2485
|  |  | 冷房潜熱 | 52.8898 | 53.2901 |  | 42.8305 | 40.3455 | 38.7157 | 46.9339
|  |  | 暖房顕熱 | -45.1076 | -43.1003 |  | -23.4587 | -43.7137 | -45.3963 | -31.6176
|  |  | 暖房潜熱 | -1.957 | -3.9841 |  | -3.7626 | -0.18551 | -2.2032 | -11.272
| 最大負荷 | kW | 冷房顕熱 | 53.5752 | 103.824 |  | 43.7018 | 50.9494 | 65.8616 | 35.4903
|  |  | 冷房潜熱 | 10.1808 | 14.3136 |  | 20.8102 | 21.2537 | 14.8643 | 21.5496
|  |  | 暖房顕熱 | -78.5232 | -112.392 |  | -35.6177 | -63.7157 | -76.3644 | -27.691
|  |  | 暖房潜熱 | -2.3688 | -4.1328 |  | -5.8666 | -6.295 | -9.1405 | -28.3308 |  |  |  | 図43 7F廊下（積算負荷） | 図44 7F廊下（最大負荷）
|  | W/m2 | 冷房顕熱 | 106.3 | 206 |  | 86.71 | 101.09 | 130.6779 | 70.4172
|  |  | 冷房潜熱 | 20.2 | 28.4 |  | 41.29 | 42.17 | 29.4926 | 42.7571
|  |  | 暖房顕熱 | -155.8 | -223 |  | -70.67 | -126.42 | -151.5167 | -54.9424
|  |  | 暖房潜熱 | -4.7 | -8.2 |  | -11.64 | -12.49 | -18.1359 | -56.2118
[14 empty] | 図45 7F自販機ｺｰﾅｰ（積算負荷） | 図46 7F自販機ｺｰﾅｰ（最大負荷）
[14 empty] | 図47 7FEVホール（積算負荷） | 図48 7FEVホール（最大負荷）
[14 empty] | 図49 7F事務室1（積算負荷） | 図50 7F事務室1（最大負荷）
[14 empty] | 図51 7F事務室2（積算負荷） | 図52 7F事務室2（最大負荷）

## 代表日
|  | 顕熱 | [55 empty] | 潜熱
|  | 事務室1NP | [7 empty] | 事務室1NEP | [7 empty] | 事務室1NWP | [7 empty] | 事務室1NI | [7 empty] | 事務室2SP | [7 empty] | 事務室2SWP | [7 empty] | 事務室2SI | [7 empty] | 事務室1NP | [7 empty] | 事務室1NEP | [7 empty] | 事務室1NWP | [7 empty] | 事務室1NI | [7 empty] | 事務室2SP | [7 empty] | 事務室2SWP | [7 empty] | 事務室2SI
|  | NewHASP |  | Popolo | BEST | BEST | BEST | E+ | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | E+ | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | E+ | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | E+ | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8 | NewHASP |  | Popolo | BEST | BEST | BEST | Tooｌ7 | Tooｌ8
|  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 | 宮田委員(IZM) |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 | 宮田委員(IZM) |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 | 宮田委員(IZM) |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 | 宮田委員(IZM) |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員 |  |  | 小野委員 | 矢島委員 | 富樫委員 | 二宮委員 | 二宮委員2 | 品川委員
2017-01-04 | 0:00 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 8:00 | -142.7 | -219.5 | -167.5007 | -117.89 | -114.27 | -83.91 | -63.1384 |  | -125.2 | -120.8 | -163.4119 | -119.31 | -115.5 | -71.82 |  |  | -132 | -129.2 | -175.0195 | -126.12 | -122.47 | -92.22 |  |  | -100.1 | -44.9 | -142.7576 | -95.63 | -91.83 | -61.16 |  |  | -106.4 | -101.7 | -154.3946 | -86.11 | -82.13 | -53.95 | -11.7278 |  | -113.7 | -115.8 | -163.8241 | -111.92 | -107.95 | -80.28 |  |  | -85.4 | -31.7 | -138.8806 | -82.44 | -78.28 | -50.17 |  |  | -4.7 | -5.9 | -6.0572 | -29.85 | -11.62 | -11.42 | -27.9984 |  | -4.7 | -5.9 | -6.0572 | -29.94 | -11.72 | -11.5 |  |  | -4.7 | -5.9 | -6.0572 | -29.9 | -11.67 | -11.47 |  |  | -4.7 | -4.9 | -6.0572 | -29.55 | -11.31 | -11.02 |  |  | -4.7 | -5.8 | -6.0572 | -29.39 | -11.15 | -10.93 | -16.2143 |  | -4.7 | -5.8 | -6.0572 | -29.48 | -11.24 | -11.04 |  |  | -4.7 | -4.9 | -6.0572 | -29.07 | -10.83 | -10.52
| 9:00 | -85.2 | -57.8 | -43.6376 | -66.04 | -63.65 | -40.54 | -13.3627 |  | -51.3 | -4.9 | -39.3619 | -50.24 | -47.72 | -10.66 |  |  | -72.6 | -31.1 | -48.8024 | -70.99 | -68.62 | -45.54 |  |  | -57.3 | -1.2 | -25.6227 | -47.87 | -45.36 | -22.36 |  |  | -42.7 | 3.9 | -25.424 | -15.29 | -12.72 | 10.42 | 34.9292 |  | -63.1 | -24.7 | -38.4269 | -62.37 | -59.84 | -38.82 |  |  | -48.5 | 16.2 | -20.4201 | -38.42 | -35.74 | -14.86 |  |  | 3.5 | 3.6 | 3.2207 | -7.85 | 0.34 | 0.53 | -1.0446 |  | 3.5 | 3.6 | 3.2207 | -7.85 | 0.34 | 0.68 |  |  | 3.5 | 3.6 | 3.2207 | -7.85 | 0.34 | 0.51 |  |  | 3.5 | 4.5 | 3.2207 | -7.85 | 0.34 | 0.65 |  |  | 3.5 | 3.6 | 3.2207 | -7.71 | 0.52 | 0.84 | 2.6746 |  | 3.5 | 3.6 | 3.2207 | -7.85 | 0.37 | 0.63 |  |  | 3.5 | 4.5 | 3.2207 | -7.77 | 0.46 | 0.81
| 10:00 | -76.1 | -49.5 | -38.7999 | -54.35 | -52.28 | -32.93 | 1.7831 |  | -40.5 | 2 | -36.4247 | -46.73 | -44.54 | -9.35 |  |  | -63.7 | -25.6 | -42.945 | -58.83 | -56.79 | -37.42 |  |  | -50.4 | 6.5 | -22.2587 | -38.2 | -36.04 | -16.28 |  |  | -19.7 | 25.7 | -14.2629 | 6.64 | 8.88 | 32.87 | 41.0674 |  | -55.3 | -19.9 | -29.8357 | -51.3 | -49.1 | -31.34 |  |  | -41.2 | 18.5 | -13.6698 | -28.63 | -26.3 | -8.29 |  |  | 4.3 | 4.6 | 3.1757 | -4.07 | 1.3 | 1.42 | 1.915 |  | 4.3 | 4.6 | 3.1757 | -3.9 | 1.46 | 1.74 |  |  | 4.3 | 4.6 | 3.1757 | -4.06 | 1.31 | 1.42 |  |  | 4.3 | 5.4 | 3.1757 | -4.05 | 1.32 | 1.53 |  |  | 4.3 | 4.6 | 3.1757 | -3.66 | 1.71 | 1.94 | 1.8049 |  | 4.3 | 4.6 | 3.1757 | -3.95 | 1.41 | 1.5 |  |  | 4.3 | 5.4 | 3.1757 | -3.87 | 1.5 | 1.67
| 11:00 | -68 | -42 | -34.1021 | -45.03 | -43.2 | -26.7 | 3.4847 |  | -43.3 | -6.3 | -35.1544 | -50.85 | -48.9 | -19.54 |  |  | -55.9 | -21.3 | -37.9217 | -49.16 | -47.35 | -30.87 |  |  | -44.4 | 8.8 | -18.9287 | -30.32 | -28.41 | -12.13 |  |  | -4.6 | 38.8 | -9.7904 | 22.52 | 24.5 | 44.17 | 41.6688 |  | -48.3 | -15.7 | -24.6214 | -42.52 | -40.57 | -25.27 |  |  | -35.7 | 19.3 | -9.5964 | -21.78 | -19.72 | -4.81 |  |  | 4.4 | 4.7 | 3.1082 | -1.96 | 1.7 | 1.63 | 2.5247 |  | 4.4 | 4.7 | 3.1082 | -1.84 | 1.81 | 1.92 |  |  | 4.4 | 4.7 | 3.1082 | -1.95 | 1.7 | 1.64 |  |  | 4.4 | 5.6 | 3.1082 | -1.93 | 1.73 | 1.79 |  |  | 4.4 | 4.7 | 3.1082 | -1.48 | 2.18 | 2.26 | 0.078197 |  | 4.4 | 4.7 | 3.1082 | -1.86 | 1.8 | 1.71 |  |  | 4.4 | 5.6 | 3.1082 | -1.76 | 1.91 | 1.93
| 12:00 | -64 | -39.3 | -36.5281 | -43.7 | -42.05 | -29.49 | 4.5572 |  | -48.5 | -17.3 | -38.5657 | -55.41 | -53.66 | -31.04 |  |  | -52.1 | -21.3 | -39.8947 | -46.68 | -45.05 | -32.5 |  |  | -41.6 | 6.8 | -22.1329 | -31.32 | -29.6 | -17.72 |  |  | 3 | 43.5 | -21.7857 | 20.29 | 22.08 | 37.46 | 42.2285 |  | -45.3 | -15.7 | -30.3089 | -40.79 | -39.03 | -27.29 |  |  | -33.6 | 16.7 | -16.0174 | -23.62 | -21.77 | -10.85 |  |  | 3.2 | 3.6 | 1.4632 | -1.94 | 0.65 | 0.45 | 2.5043 |  | 3.2 | 3.6 | 1.4632 | -1.92 | 0.67 | 0.55 |  |  | 3.2 | 3.6 | 1.4632 | -1.94 | 0.65 | 0.46 |  |  | 3.2 | 4.5 | 1.4632 | -1.92 | 0.67 | 0.53 |  |  | 3.2 | 3.6 | 1.4632 | -1.62 | 0.97 | 0.84 | -1.0534 |  | 3.2 | 3.6 | 1.4632 | -1.89 | 0.7 | 0.49 |  |  | 3.2 | 4.5 | 1.4632 | -1.83 | 0.76 | 0.61
| 13:00 | -57.7 | -33.8 | -26.7733 | -29.16 | -27.68 | -16.66 | -2.1915 |  | -44.7 | -17.5 | -28.3319 | -40.59 | -39.01 | -18.73 |  |  | -42.5 | -13.7 | -28.0345 | -25.39 | -23.93 | -11.26 |  |  | -36.9 | 7.5 | -13.4565 | -19.03 | -17.49 | -6.95 |  |  | 0.7 | 37.3 | -14.1984 | 11.99 | 13.59 | 26.5 | 39.9329 |  | -36.5 | -8.2 | -19.5384 | -20.19 | -18.61 | -6.41 |  |  | -29.5 | 17.1 | -7.7961 | -12.14 | -10.48 | -0.54 |  |  | 3.2 | 3.5 | 3.0407 | 0.12 | 2.04 | 1.8 | 4.3049e-14 |  | 3.2 | 3.5 | 3.0407 | 0.12 | 2.04 | 1.84 |  |  | 3.2 | 3.5 | 3.0407 | 0.13 | 2.05 | 1.82 |  |  | 3.2 | 4.5 | 3.0407 | 0.13 | 2.06 | 1.89 |  |  | 3.2 | 3.5 | 3.0407 | 0.63 | 2.56 | 2.41 | -0.7803 |  | 3.2 | 3.5 | 3.0407 | 0.2 | 2.12 | 1.88 |  |  | 3.2 | 4.5 | 3.0407 | 0.27 | 2.2 | 2.01
| 14:00 | -49.7 | -26.2 | -24.8915 | -24.62 | -23.26 | -15.06 | 5.7506 |  | -37 | -12 | -25.9798 | -35.49 | -34.04 | -17.21 |  |  | -27.8 | 0.1 | -21.2969 | -13.99 | -12.65 | -3.33 |  |  | -30 | 11.5 | -11.4712 | -13.59 | -12.18 | -4.32 |  |  | -4.1 | 28.9 | -7.0359 | 10.29 | 11.76 | 21.35 | 38.6457 |  | -22.6 | 5.5 | -10.797 | -9.37 | -7.93 | 1.21 |  |  | -23.1 | 20.8 | -3.7906 | -7.34 | -5.83 | 1.76 |  |  | 4.2 | 4.6 | 3.1307 | 0.78 | 2.25 | 1.96 | 2.5557 |  | 4.2 | 4.6 | 3.1307 | 0.76 | 2.23 | 1.99 |  |  | 4.2 | 4.6 | 3.1307 | 0.82 | 2.29 | 2.06 |  |  | 4.2 | 5.6 | 3.1307 | 0.8 | 2.28 | 2.04 |  |  | 4.2 | 4.6 | 3.1307 | 1.15 | 2.62 | 2.4 | 2.4327 |  | 4.2 | 4.6 | 3.1307 | 0.88 | 2.35 | 2.11 |  |  | 4.2 | 5.6 | 3.1307 | 0.93 | 2.4 | 2.15
| 15:00 | -46.5 | -24.1 | -24.1047 | -22.16 | -20.91 | -15.35 | 5.152 |  | -34.2 | -12 | -24.8899 | -32.46 | -31.14 | -17.44 |  |  | -14.1 | 12.2 | -20.7732 | 5.2 | 6.44 | 13.59 |  |  | -25.8 | 12.5 | -10.2266 | -9.37 | -8.08 | -2.35 |  |  | -2 | 28.8 | -12.2228 | 19.03 | 20.37 | 27.75 | 40.5571 |  | -9.6 | 17.5 | -12.123 | 9.31 | 10.64 | 17.86 |  |  | -19.5 | 21.4 | -4.2814 | -3.66 | -2.28 | 3.44 |  |  | 4.3 | 4.6 | 3.1757 | 1.33 | 2.46 | 2.15 | 2.5375 |  | 4.3 | 4.6 | 3.1757 | 1.31 | 2.44 | 2.17 |  |  | 4.3 | 4.6 | 3.1757 | 1.42 | 2.55 | 2.29 |  |  | 4.3 | 5.6 | 3.1757 | 1.38 | 2.51 | 2.25 |  |  | 4.3 | 4.6 | 3.1757 | 1.65 | 2.78 | 2.53 | 2.2545 |  | 4.3 | 4.6 | 3.1757 | 1.47 | 2.6 | 2.34 |  |  | 4.3 | 5.6 | 3.1757 | 1.49 | 2.62 | 2.35
| 16:00 | -44.3 | -23.3 | -24.5977 | -20.98 | -19.79 | -17.14 | 4.2284 |  | -32.5 | -13.1 | -24.9963 | -30.8 | -29.54 | -19.16 |  |  | -7.6 | 16.4 | -25.0957 | 1.43 | 2.6 | 7.23 |  |  | -22.2 | 13.3 | -9.8558 | -5.94 | -4.71 | -0.83 |  |  | -4 | 24 | -20.0948 | 5.98 | 7.25 | 11.97 | 29.9223 |  | -3.6 | 21.7 | -18.9174 | 5.09 | 6.35 | 11.25 |  |  | -16.2 | 21.9 | -6.3916 | -0.66 | 0.65 | 4.76 |  |  | 4.4 | 4.7 | 3.1757 | 1.69 | 2.59 | 2.23 | 2.544 |  | 4.4 | 4.7 | 3.1757 | 1.66 | 2.56 | 2.25 |  |  | 4.4 | 4.7 | 3.1757 | 1.88 | 2.78 | 2.51 |  |  | 4.4 | 5.6 | 3.1757 | 1.75 | 2.66 | 2.37 |  |  | 4.4 | 4.7 | 3.1757 | 2.04 | 2.94 | 2.67 | 2.5851 |  | 4.4 | 4.7 | 3.1757 | 1.93 | 2.83 | 2.55 |  |  | 4.4 | 5.6 | 3.1757 | 1.85 | 2.76 | 2.47
| 17:00 | -42.7 | -23 | -23.5053 | -20.27 | -19.14 | -19.03 | 3.1927 |  | -31.8 | -14.4 | -23.8692 | -29.73 | -28.53 | -21.09 |  |  | -20 | -0.6 | -24.1796 | -19.86 | -18.74 | -18.48 |  |  | -18.9 | 14.1 | -8.5283 | -3.05 | -1.89 | 0.44 |  |  | -16.5 | 7 | -20.3446 | -9.49 | -8.28 | -7.33 | 19.6709 |  | -16.3 | 4.5 | -18.5764 | -16.58 | -15.39 | -14.68 |  |  | -13.3 | 22.4 | -5.5698 | 1.9 | 3.14 | 5.89 |  |  | 4.4 | 4.7 | 3.1757 | 1.89 | 2.65 | 2.22 | 2.5514 |  | 4.4 | 4.7 | 3.1757 | 1.87 | 2.62 | 2.25 |  |  | 4.4 | 4.7 | 3.1757 | 2.07 | 2.83 | 2.52 |  |  | 4.4 | 5.6 | 3.1757 | 1.99 | 2.74 | 2.42 |  |  | 4.4 | 4.7 | 3.1757 | 2.16 | 2.91 | 2.6 | 2.5517 |  | 4.4 | 4.7 | 3.1757 | 2.12 | 2.87 | 2.56 |  |  | 4.4 | 5.6 | 3.1757 | 2.08 | 2.83 | 2.51
| 18:00 | -41.9 | -23.3 | -25.3047 | -20.9 | -19.81 | -21.96 | 3.1531 |  | -31.9 | -16.2 | -25.7551 | -30.22 | -29.06 | -24.23 |  |  | -30.7 | -15.2 | -26.0777 | -21.7 | -20.61 | -23.02 |  |  | -16.7 | 13.7 | -9.6128 | -3.15 | -2.03 | -1.29 |  |  | -23.7 | -3.7 | -23.0498 | -11.72 | -10.56 | -11.85 | 18.5335 |  | -27.3 | -10.2 | -20.685 | -18.75 | -17.61 | -19.42 |  |  | -11.4 | 21.7 | -6.9696 | 1.56 | 2.75 | 4.07 |  |  | 3 | 3.3 | 1.2207 | 0.26 | 0.91 | 0.52 | 2.5492 |  | 3 | 3.3 | 1.2207 | 0.25 | 0.89 | 0.53 |  |  | 3 | 3.3 | 1.2207 | 0.29 | 0.93 | 0.55 |  |  | 3 | 4.2 | 1.2207 | 0.32 | 0.96 | 0.64 |  |  | 3 | 3.3 | 1.2207 | 0.34 | 0.98 | 0.6 | 2.5492 |  | 3 | 3.3 | 1.2207 | 0.3 | 0.95 | 0.57 |  |  | 3 | 4.2 | 1.2207 | 0.36 | 1.01 | 0.68
| 19:00 | -44.1 | -26.6 | -28.6464 | -24.87 | -23.8 | -28.42 | 0.03386 |  | -34.9 | -20.8 | -29.3238 | -34.1 | -32.98 | -31.02 |  |  | -33.5 | -19.6 | -29.6355 | -26.25 | -25.19 | -30.2 |  |  | -18.3 | 9.8 | -12.7242 | -6.45 | -5.35 | -7.76 |  |  | -27 | -8.5 | -26.703 | -16.76 | -15.63 | -19.23 | 14.7539 |  | -30.5 | -14.7 | -24.3789 | -23.61 | -22.49 | -26.78 |  |  | -13.2 | 17.5 | -10.3829 | -1.96 | -0.8 | -2.47 |  |  | 1.1 | 1.4 | 0.2632 | -0.29 | 0.26 | -0.09 | 0.060063 |  | 1.1 | 1.4 | 0.2632 | -0.3 | 0.25 | -0.09 |  |  | 1.1 | 1.4 | 0.2632 | -0.28 | 0.26 | -0.08 |  |  | 1.1 | 2.2 | 0.2632 | -0.25 | 0.29 | -0.02 |  |  | 1.1 | 1.4 | 0.2632 | -0.25 | 0.29 | -0.05 | 0.93919 |  | 1.1 | 1.4 | 0.2632 | -0.27 | 0.27 | -0.07 |  |  | 1.1 | 2.2 | 0.2632 | -0.23 | 0.32 | 0.01
| 20:00 | -45.6 | -29.1 | -30.7291 | -25.18 | -24.19 | -29.12 | -5.1446 |  | -37.1 | -24.5 | -31.4826 | -34.28 | -33.24 | -31.92 |  |  | -35.7 | -23.3 | -31.8159 | -26.95 | -25.96 | -31.24 |  |  | -19.6 | 6.2 | -13.8564 | -7.02 | -6.01 | -8.92 |  |  | -29.6 | -12.4 | -29.6151 | -17.95 | -16.9 | -20.58 | 9.1415 |  | -33 | -18.4 | -26.6641 | -24.58 | -23.54 | -28 |  |  | -14.7 | 13.7 | -11.7716 | -2.77 | -1.71 | -3.77 |  |  | 0.2 | 0.5 | -0.0918 | -0.8 | -0.25 | -0.63 | 3.1726e-06 |  | 0.2 | 0.5 | -0.0918 | -0.8 | -0.26 | -0.62 |  |  | 0.2 | 0.5 | -0.0918 | -0.8 | -0.25 | -0.62 |  |  | 0.2 | 1.4 | -0.0918 | -0.77 | -0.22 | -0.59 |  |  | 0.2 | 0.5 | -0.0918 | -0.78 | -0.23 | -0.6 | 0.20971 |  | 0.2 | 0.5 | -0.0918 | -0.79 | -0.24 | -0.62 |  |  | 0.2 | 1.4 | -0.0918 | -0.76 | -0.21 | -0.57
| 21:00 | -45.6 | -31 | -39.7778 | -34.39 | -33.41 | -40.27 | -7.4935 |  | -37.8 | -27.4 | -40.9398 | -43.26 | -42.22 | -43.18 |  |  | -36.5 | -26.3 | -41.2926 | -36.4 | -35.42 | -42.56 |  |  | -19.3 | 2.3 | -21.4364 | -15.02 | -14.01 | -18.98 |  |  | -30.7 | -15.7 | -39.2036 | -27.86 | -26.82 | -32.23 | 6.3861 |  | -34.1 | -21.6 | -36.1217 | -34.27 | -33.24 | -39.48 |  |  | -14.7 | 9.4 | -19.8777 | -11.04 | -9.99 | -13.92 |  |  | -0.2 | -0.4 | -0.8693 | -1.4 | -0.91 | -1.25 | -0.13218 |  | -0.2 | -0.4 | -0.8693 | -1.4 | -0.91 | -1.25 |  |  | -0.2 | -0.4 | -0.8693 | -1.4 | -0.91 | -1.25 |  |  | -0.2 | 0.6 | -0.8693 | -1.4 | -0.91 | -1.25 |  |  | -0.2 | -0.4 | -0.8693 | -1.4 | -0.91 | -1.25 | -0.13982 |  | -0.2 | -0.4 | -0.8693 | -1.4 | -0.91 | -1.25 |  |  | -0.2 | 0.6 | -0.8693 | -1.4 | -0.91 | -1.25
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2017-04-05 | 0:00 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 8:00 | -24.3 | -47.1 | -21.2848 | -14.49 | -13.13 | -10.36 | -51.0223 |  | -2.2 | -5.4 | -16.0907 | 1.17 | 2.57 | 13.72 |  |  | -24.7 | -34.2 | -22.8175 | -19.31 | -17.93 | -15.37 |  |  | -0.7 | 6.1 | -9.0029 | -0.22 | 1.19 | 1.42 |  |  | -14.7 | -26.3 | -26.205 | -6.33 | -4.94 | -1.68 | -15.5382 |  | -22.3 | -37.9 | -23.6503 | -17.19 | -15.79 | -12.73 |  |  | 3.4 | 11.6 | -10.8072 | 2.53 | 3.96 | 4.46 |  |  | -6.3 | -2.8 | -5.5094 | -6.87 | -5.32 | -8.36 | -12.434 |  | -6.3 | -2.8 | -5.5094 | -6.51 | -4.96 | -7.78 |  |  | -6.3 | -2.8 | -5.5094 | -6.97 | -5.41 | -8.36 |  |  | -6.3 | -1.2 | -5.5094 | -6.44 | -4.88 | -7.97 |  |  | -6.3 | -2.3 | -5.5094 | -6.71 | -5.15 | -8.2 | -5.2794 |  | -6.3 | -2.4 | -5.5094 | -6.87 | -5.31 | -8.36 |  |  | -6.3 | -0.8 | -5.5094 | -6.31 | -4.75 | -7.78
| 9:00 | -4.5 | -0.5 | 10.339 | 2.18 | 3.05 | 7.9 | 0.86821 |  | 18.3 | 28.4 | 13.1031 | 16.14 | 17.04 | 29.45 |  |  | -3.9 | 2.6 | 9.3047 | -1.24 | -0.37 | 4.57 |  |  | 11.7 | 20.2 | 16.185 | 10.63 | 11.53 | 13.39 |  |  | 7.1 | 14.3 | 9.5446 | 14.53 | 15.42 | 20.95 | -1.2401 |  | -3 | 2.8 | 9.5023 | -0.11 | 0.77 | 5.84 |  |  | 14.4 | 22.9 | 16.8072 | 13.1 | 14 | 15.84 |  |  | 2.6 | 3.6 | 2.7849 | -0.02 | 2.02 | 1.43 | -2.8411 |  | 2.6 | 3.6 | 2.7849 | 0.09 | 2.12 | 1.7 |  |  | 2.6 | 3.6 | 2.7849 | -0.06 | 1.97 | 1.4 |  |  | 2.6 | 5 | 2.7849 | 0.14 | 2.18 | 1.57 |  |  | 2.6 | 3.7 | 2.7849 | 0.06 | 2.1 | 1.53 | -2.9083 |  | 2.6 | 3.6 | 2.7849 | -0.04 | 2 | 1.42 |  |  | 2.6 | 5.1 | 2.7849 | 0.18 | 2.22 | 1.61
| 10:00 | -0.7 | 3.7 | 13.9206 | 7.77 | 8.54 | 13 | 9.7126 |  | 18.7 | 27.7 | 15.1394 | 15.21 | 16.01 | 29.25 |  |  | -0.1 | 6.4 | 13.0067 | 4.48 | 5.25 | 9.87 |  |  | 13.2 | 21.8 | 18.0344 | 13 | 13.79 | 15.56 |  |  | 16.1 | 23.8 | 13.7358 | 23.2 | 23.98 | 31.17 | 20.245 |  | 0.7 | 6.5 | 13.2114 | 5.48 | 6.25 | 11 |  |  | 16 | 23.6 | 19.1854 | 15.76 | 16.55 | 18.27 |  |  | 3.6 | 4.2 | 2.8524 | 1.17 | 2.6 | 2.09 | 1.2133 |  | 3.6 | 4.2 | 2.8524 | 1.26 | 2.68 | 2.34 |  |  | 3.6 | 4.2 | 2.8524 | 1.14 | 2.56 | 2.07 |  |  | 3.6 | 5.5 | 2.8524 | 1.29 | 2.72 | 2.18 |  |  | 3.6 | 4.2 | 2.8524 | 1.28 | 2.7 | 2.24 | 1.9016 |  | 3.6 | 4.2 | 2.8524 | 1.16 | 2.58 | 2.08 |  |  | 3.6 | 5.5 | 2.8524 | 1.33 | 2.76 | 2.22
| 11:00 | 3.1 | 8.6 | 15.8557 | 11.75 | 12.42 | 17.84 | 11.4425 |  | 13.9 | 21.2 | 16.1474 | 11.15 | 11.85 | 22.97 |  |  | 3.7 | 10.4 | 15.048 | 8.63 | 9.3 | 14.8 |  |  | 14.5 | 22.5 | 19.214 | 14.78 | 15.47 | 17.03 |  |  | 22 | 29.8 | 16.0874 | 27.27 | 27.95 | 34.16 | 23.3484 |  | 4.3 | 10.6 | 15.3248 | 9.51 | 10.19 | 15.82 |  |  | 17.1 | 24.1 | 20.6895 | 17.28 | 17.98 | 19.49 |  |  | 3.9 | 4.4 | 2.9424 | 1.82 | 2.88 | 2.41 | 2.27 |  | 3.9 | 4.4 | 2.9424 | 1.86 | 2.92 | 2.56 |  |  | 3.9 | 4.4 | 2.9424 | 1.78 | 2.84 | 2.38 |  |  | 3.9 | 5.6 | 2.9424 | 1.91 | 2.98 | 2.46 |  |  | 3.9 | 4.4 | 2.9424 | 1.95 | 3.01 | 2.58 | 2.4101 |  | 3.9 | 4.4 | 2.9424 | 1.8 | 2.86 | 2.4 |  |  | 3.9 | 5.6 | 2.9424 | 1.96 | 3.02 | 2.51
| 12:00 | 3.5 | 9.2 | 9.71 | 6.49 | 7.11 | 11.71 | 12.1941 |  | 7.5 | 12.9 | 9.6586 | 2.1 | 2.74 | 10.55 |  |  | 4.2 | 10.5 | 9.1262 | 4.68 | 5.3 | 9.94 |  |  | 12.9 | 19.7 | 13.2365 | 8.82 | 9.45 | 9.54 |  |  | 22.1 | 28.9 | 9.8883 | 22.24 | 22.86 | 27.47 | 24.3712 |  | 4.7 | 10.7 | 9.3888 | 5.46 | 6.08 | 10.88 |  |  | 15.4 | 21.3 | 14.4822 | 11.12 | 11.75 | 11.85 |  |  | 2.9 | 3.3 | 1.3199 | 0.55 | 1.37 | 0.96 | 2.22 |  | 2.9 | 3.3 | 1.3199 | 0.54 | 1.36 | 0.99 |  |  | 2.9 | 3.3 | 1.3199 | 0.53 | 1.35 | 0.95 |  |  | 2.9 | 4.5 | 1.3199 | 0.6 | 1.42 | 0.96 |  |  | 2.9 | 3.3 | 1.3199 | 0.63 | 1.45 | 1.04 | 2.5082 |  | 2.9 | 3.3 | 1.3199 | 0.54 | 1.35 | 0.96 |  |  | 2.9 | 4.5 | 1.3199 | 0.62 | 1.44 | 0.99
| 13:00 | 5.7 | 11.2 | 17.3629 | 15.26 | 15.79 | 21.54 | 4.7797 |  | 8.4 | 13.1 | 17.83 | 10.75 | 11.3 | 21.09 |  |  | 9.2 | 15.2 | 17.761 | 18.95 | 19.48 | 26.74 |  |  | 13.7 | 19.9 | 19.8488 | 16.49 | 17.03 | 18.46 |  |  | 22.6 | 28.9 | 16.9685 | 28.67 | 29.21 | 34.57 | 14.7175 |  | 9.6 | 15.5 | 17.733 | 19.64 | 20.17 | 27.61 |  |  | 16 | 21.4 | 21.1018 | 18.56 | 19.1 | 20.56 |  |  | 2.9 | 3.4 | 2.8749 | 2.39 | 3.09 | 2.68 | 0.82276 |  | 2.9 | 3.4 | 2.8749 | 2.36 | 3.06 | 2.68 |  |  | 2.9 | 3.4 | 2.8749 | 2.37 | 3.07 | 2.68 |  |  | 2.9 | 4.5 | 2.8749 | 2.44 | 3.14 | 2.65 |  |  | 2.9 | 3.4 | 2.8749 | 2.53 | 3.23 | 2.81 | 1.4917 |  | 2.9 | 3.4 | 2.8749 | 2.38 | 3.08 | 2.69 |  |  | 2.9 | 4.5 | 2.8749 | 2.48 | 3.18 | 2.69
| 14:00 | 10.7 | 16.6 | 16.7787 | 16.98 | 17.46 | 22.46 | 12.4597 |  | 13.4 | 18.1 | 17.7564 | 12.6 | 13.1 | 22.17 |  |  | 17.9 | 24.3 | 17.0533 | 22.6 | 23.08 | 28.09 |  |  | 17.1 | 23.4 | 19.4414 | 18.18 | 18.67 | 19.73 |  |  | 23.3 | 29.2 | 15.4054 | 25.72 | 26.21 | 30.41 | 19.9321 |  | 18.2 | 24.6 | 16.8465 | 23.2 | 23.69 | 28.9 |  |  | 19.3 | 24.9 | 20.3845 | 20.06 | 20.55 | 21.67 |  |  | 4 | 4.4 | 2.7174 | 2.55 | 3.18 | 2.77 | 2.2102 |  | 4 | 4.4 | 2.7174 | 2.5 | 3.13 | 2.77 |  |  | 4 | 4.4 | 2.7174 | 2.56 | 3.19 | 2.78 |  |  | 4 | 5.6 | 2.7174 | 2.61 | 3.24 | 2.73 |  |  | 4 | 4.4 | 2.7174 | 2.67 | 3.3 | 2.86 | 2.1219 |  | 4 | 4.4 | 2.7174 | 2.57 | 3.2 | 2.79 |  |  | 4 | 5.6 | 2.7174 | 2.64 | 3.27 | 2.77
| 15:00 | 12.1 | 17.4 | 15.8351 | 16.71 | 17.15 | 21.26 | 11.5242 |  | 14.7 | 18.9 | 17.1007 | 12.53 | 12.98 | 21.1 |  |  | 16.7 | 22 | 18.0266 | 17.57 | 18.01 | 20.59 |  |  | 18 | 23.9 | 19.2959 | 19.1 | 19.55 | 20.43 |  |  | 19.7 | 24.3 | 14.8376 | 20.74 | 21.19 | 23.17 | 16.7736 |  | 16.9 | 22.4 | 18.1649 | 18.11 | 18.55 | 21.35 |  |  | 20 | 25.4 | 20.4521 | 20.84 | 21.29 | 22.26 |  |  | 3.9 | 4.3 | 2.8524 | 2.44 | 3.07 | 2.59 | 2.0354 |  | 3.9 | 4.3 | 2.8524 | 2.39 | 3.02 | 2.59 |  |  | 3.9 | 4.3 | 2.8524 | 2.46 | 3.1 | 2.59 |  |  | 3.9 | 5.6 | 2.8524 | 2.5 | 3.14 | 2.57 |  |  | 3.9 | 4.3 | 2.8524 | 2.53 | 3.16 | 2.64 | 2.0362 |  | 3.9 | 4.3 | 2.8524 | 2.47 | 3.11 | 2.6 |  |  | 3.9 | 5.6 | 2.8524 | 2.53 | 3.17 | 2.59
| 16:00 | 11.3 | 15.8 | 13.6559 | 14.35 | 14.78 | 18.16 | 10.7417 |  | 13.8 | 17.1 | 15.4269 | 10.4 | 10.85 | 18.12 |  |  | 16.7 | 21.6 | 14.8224 | 25.56 | 25.99 | 30.43 |  |  | 18.7 | 24.3 | 18.0822 | 19.66 | 20.1 | 20.83 |  |  | 16.8 | 20.4 | 12.0806 | 18.98 | 19.42 | 22.06 | 15.5571 |  | 16.9 | 21.9 | 15.1687 | 26.03 | 26.47 | 31.15 |  |  | 20.6 | 25.7 | 19.0602 | 21.33 | 21.77 | 22.62 |  |  | 3.8 | 4.3 | 2.9199 | 2.68 | 3.23 | 2.77 | 2.2354 |  | 3.8 | 4.3 | 2.9199 | 2.63 | 3.18 | 2.78 |  |  | 3.8 | 4.3 | 2.9199 | 2.68 | 3.23 | 2.77 |  |  | 3.8 | 5.6 | 2.9199 | 2.76 | 3.31 | 2.78 |  |  | 3.8 | 4.3 | 2.9199 | 2.74 | 3.28 | 2.8 | 2.2313 |  | 3.8 | 4.3 | 2.9199 | 2.69 | 3.24 | 2.78 |  |  | 3.8 | 5.6 | 2.9199 | 2.78 | 3.33 | 2.81
| 17:00 | 8.9 | 12.7 | 11.9193 | 11.88 | 12.31 | 14.33 | 8.7466 |  | 11.3 | 13.7 | 13.9655 | 8.08 | 8.52 | 14.36 |  |  | 14.4 | 18.3 | 13.2211 | 12.22 | 12.65 | 13.95 |  |  | 19.2 | 24.6 | 17.3687 | 20.02 | 20.47 | 21.07 |  |  | 14.2 | 17.1 | 10.076 | 14.55 | 14.99 | 16.79 | 12.5051 |  | 14.6 | 18.7 | 13.7978 | 12.64 | 13.08 | 14.63 |  |  | 21 | 26 | 18.2984 | 21.68 | 22.12 | 22.86 |  |  | 4 | 4.4 | 2.8974 | 2.81 | 3.3 | 2.83 | 2.3319 |  | 4 | 4.4 | 2.8974 | 2.76 | 3.25 | 2.84 |  |  | 4 | 4.4 | 2.8974 | 2.87 | 3.37 | 2.93 |  |  | 4 | 5.6 | 2.8974 | 2.9 | 3.4 | 2.9 |  |  | 4 | 4.4 | 2.8974 | 2.86 | 3.35 | 2.89 | 2.3317 |  | 4 | 4.4 | 2.8974 | 2.88 | 3.37 | 2.94 |  |  | 4 | 5.6 | 2.8974 | 2.92 | 3.42 | 2.92
| 18:00 | 5.6 | 8.5 | 8.308 | 7.04 | 7.48 | 8.06 | 7.6904 |  | 7.8 | 9.2 | 10.26 | 3.29 | 3.75 | 8.07 |  |  | 6.9 | 8.8 | 9.5136 | 6.34 | 6.78 | 7.09 |  |  | 18.7 | 23.8 | 14.8254 | 17.92 | 18.37 | 18.61 |  |  | 10.4 | 12.3 | 6.0923 | 9.47 | 9.92 | 10.24 | 11.404 |  | 7.1 | 9.2 | 10.2193 | 6.72 | 7.16 | 7.73 |  |  | 20.5 | 25.2 | 15.6051 | 19.59 | 20.04 | 20.43 |  |  | 2.6 | 3.1 | 0.87486 | 0.59 | 1.07 | 0.6 | 2.3299 |  | 2.6 | 3.1 | 0.87486 | 0.57 | 1.05 | 0.61 |  |  | 2.6 | 3.1 | 0.87486 | 0.59 | 1.07 | 0.61 |  |  | 2.6 | 4.2 | 0.87486 | 0.65 | 1.13 | 0.67 |  |  | 2.6 | 3.1 | 0.87486 | 0.61 | 1.09 | 0.62 | 2.3299 |  | 2.6 | 3.1 | 0.87486 | 0.59 | 1.08 | 0.61 |  |  | 2.6 | 4.2 | 0.87486 | 0.66 | 1.14 | 0.68
| 19:00 | -0.3 | 2.1 | 3.063 | 0.72 | 1.18 | -0.43 | 4.1076 |  | 1.4 | 2.5 | 4.7163 | -3.16 | -2.68 | -0.7 |  |  | 0.7 | 2.3 | 3.9986 | -0.28 | 0.19 | -1.79 |  |  | 14.7 | 19.5 | 10.3495 | 12.73 | 13.2 | 11.33 |  |  | 4.2 | 5.6 | 0.78051 | 2.91 | 3.38 | 1.58 | 7.7785 |  | 0.9 | 2.7 | 4.8143 | 0.07 | 0.53 | -1.18 |  |  | 16.5 | 20.8 | 10.9146 | 14.43 | 14.91 | 13.22 |  |  | 0.6 | 1.1 | 0.18736 | -0.31 | 0.17 | -0.3 | 0.4907 |  | 0.6 | 1.1 | 0.18736 | -0.32 | 0.16 | -0.3 |  |  | 0.6 | 1.1 | 0.18736 | -0.31 | 0.17 | -0.3 |  |  | 0.6 | 2.2 | 0.18736 | -0.27 | 0.21 | -0.25 |  |  | 0.6 | 1.1 | 0.18736 | -0.3 | 0.18 | -0.29 | 0.80864 |  | 0.6 | 1.1 | 0.18736 | -0.31 | 0.17 | -0.3 |  |  | 0.6 | 2.2 | 0.18736 | -0.26 | 0.22 | -0.24
| 20:00 | -4.8 | -2.4 | 0.48622 | -1.83 | -1.38 | -2.82 | -1.177 |  | -3.5 | -2.2 | 1.9523 | -5.83 | -5.36 | -3.35 |  |  | -4.1 | -2.4 | 1.2613 | -3.07 | -2.61 | -4.39 |  |  | 11.1 | 15.6 | 8.2824 | 10.28 | 10.74 | 9.2 |  |  | -0.5 | 0.9 | -1.9026 | 0.13 | 0.59 | -0.96 | 2.4598 |  | -3.9 | -1.9 | 2.137 | -2.76 | -2.31 | -3.82 |  |  | 12.9 | 16.9 | 8.7127 | 12 | 12.46 | 11.11 |  |  | -0.1 | 0.3 | -0.077641 | -0.58 | -0.16 | -0.56 | -1.1634 |  | -0.1 | 0.3 | -0.077641 | -0.59 | -0.17 | -0.56 |  |  | -0.1 | 0.3 | -0.077641 | -0.58 | -0.16 | -0.56 |  |  | -0.1 | 1.4 | -0.077641 | -0.55 | -0.13 | -0.53 |  |  | -0.1 | 0.3 | -0.077641 | -0.58 | -0.15 | -0.56 | 0.21131 |  | -0.1 | 0.3 | -0.077641 | -0.58 | -0.16 | -0.56 |  |  | -0.1 | 1.4 | -0.077641 | -0.55 | -0.12 | -0.52
| 21:00 | -6.8 | -5.9 | -9.5323 | -11.76 | -11.31 | -14.05 | -3.4924 |  | -5.8 | -5.9 | -8.5289 | -15.72 | -15.26 | -14.71 |  |  | -6.3 | -6.1 | -9.2 | -13.11 | -12.66 | -15.7 |  |  | 9.3 | 11.3 | -0.28217 | 0.96 | 1.41 | -1.4 |  |  | -2.8 | -2.8 | -11.9981 | -9.95 | -9.5 | -12.27 | 0.08056 |  | -6.1 | -5.6 | -8.1298 | -12.83 | -12.38 | -15.15 |  |  | 11 | 12.5 | -0.25194 | 2.58 | 3.03 | 0.51 |  |  | -0.2 | -0.4 | -0.90014 | -1.25 | -0.89 | -1.22 | -0.9879 |  | -0.2 | -0.4 | -0.90014 | -1.25 | -0.89 | -1.22 |  |  | -0.2 | -0.4 | -0.90014 | -1.25 | -0.89 | -1.22 |  |  | -0.2 | 0.6 | -0.90014 | -1.25 | -0.89 | -1.22 |  |  | -0.2 | -0.4 | -0.90014 | -1.25 | -0.89 | -1.22 | -1.8005 |  | -0.2 | -0.4 | -0.90014 | -1.25 | -0.89 | -1.22 |  |  | -0.2 | 0.6 | -0.90014 | -1.25 | -0.89 | -1.22
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2017-07-18 | 0:00 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 8:00 | 94.9 | 211.3 | 144.3169 | 106.85 | 106.83 | 103.32 | 64.303 |  | 109.1 | 153.2 | 154.2562 | 138.61 | 138.6 | 131.45 |  |  | 92.4 | 132.5 | 148.6001 | 112.01 | 112 | 108.94 |  |  | 71.9 | 72.9 | 127.4893 | 89.84 | 89.82 | 82.2 |  |  | 89.2 | 182.9 | 132.7264 | 103.78 | 103.72 | 99.32 | 62.674 |  | 90.8 | 177.4 | 132.9667 | 109.21 | 109.16 | 105.33 |  |  | 72.3 | 137.6 | 118.4833 | 86.95 | 86.89 | 78.26 |  |  | 20.2 | 23.7 | 29.4926 | 76.3 | 41.59 | 41.63 | 40.9961 |  | 20.2 | 23.7 | 29.4926 | 76.64 | 41.93 | 42.15 |  |  | 20.2 | 23.7 | 29.4926 | 76.34 | 41.63 | 41.66 |  |  | 20.2 | 21.9 | 29.4926 | 76.08 | 41.37 | 41.24 |  |  | 20.2 | 23.2 | 29.4926 | 76.09 | 41.38 | 41.28 | 44.0361 |  | 20.2 | 23.2 | 29.4926 | 76.19 | 41.47 | 41.41 |  |  | 20.2 | 21.3 | 29.4926 | 75.85 | 41.14 | 40.89
| 9:00 | 79 | 87.9 | 72.3577 | 83.04 | 82.89 | 81.48 | 60.0519 |  | 95.3 | 86.8 | 79.4865 | 113.36 | 113.22 | 108.58 |  |  | 75.1 | 66.3 | 75.8512 | 86.43 | 86.28 | 85.25 |  |  | 60.5 | 46.2 | 55.2505 | 65.47 | 65.33 | 58.91 |  |  | 76.7 | 77.9 | 70.5744 | 83.54 | 83.37 | 81.76 | 58.6604 |  | 75.2 | 73.8 | 68.9992 | 84.97 | 84.81 | 83.57 |  |  | 61.9 | 43.9 | 54.857 | 63.64 | 63.47 | 56.54 |  |  | 10.1 | 9.9 | 5.7554 | 28.9 | 11.63 | 11.25 | 9.8516 |  | 10.1 | 9.9 | 5.7554 | 29.01 | 11.74 | 11.5 |  |  | 10.1 | 9.9 | 5.7554 | 28.89 | 11.62 | 11.25 |  |  | 10.1 | 8.2 | 5.7554 | 28.93 | 11.66 | 11.14 |  |  | 10.1 | 9.9 | 5.7554 | 28.85 | 11.58 | 11.19 | 10.902 |  | 10.1 | 9.9 | 5.7554 | 28.85 | 11.59 | 11.2 |  |  | 10.1 | 8.1 | 5.7554 | 28.84 | 11.57 | 11.05
| 10:00 | 78.3 | 86.7 | 71.504 | 81.08 | 80.89 | 81.64 | 58.7771 |  | 92.1 | 84.1 | 77.2768 | 105.15 | 104.97 | 103.35 |  |  | 74.5 | 67.3 | 74.6445 | 84.24 | 84.06 | 85.29 |  |  | 58.6 | 39.7 | 54.3189 | 61.69 | 61.5 | 56.47 |  |  | 78 | 79.1 | 71.2359 | 84.74 | 84.53 | 85.48 | 57.358 |  | 74.6 | 74.6 | 68.4748 | 82.96 | 82.76 | 83.78 |  |  | 59.4 | 40.4 | 54.3156 | 59.45 | 59.24 | 53.7 |  |  | 8.2 | 7.6 | 5.9354 | 21.45 | 10.09 | 10.11 | 6.9823 |  | 8.2 | 7.6 | 5.9354 | 21.54 | 10.19 | 10.36 |  |  | 8.2 | 7.6 | 5.9354 | 21.42 | 10.07 | 10.09 |  |  | 8.2 | 5.9 | 5.9354 | 21.46 | 10.11 | 9.95 |  |  | 8.2 | 7.6 | 5.9354 | 21.43 | 10.08 | 10.09 | 8.3371 |  | 8.2 | 7.6 | 5.9354 | 21.4 | 10.05 | 10.06 |  |  | 8.2 | 5.9 | 5.9354 | 21.38 | 10.03 | 9.88
| 11:00 | 77 | 84.7 | 69.6557 | 77.72 | 77.51 | 81.91 | 57.9857 |  | 83.3 | 75.7 | 73.9404 | 93.27 | 93.07 | 92.16 |  |  | 73.4 | 68 | 72.8772 | 80.79 | 80.59 | 85.41 |  |  | 56.8 | 38.5 | 52.8391 | 58.04 | 57.84 | 54.58 |  |  | 79.3 | 80.4 | 71.3415 | 84.35 | 84.12 | 86.72 | 56.2713 |  | 73.6 | 74.4 | 67.7447 | 79.66 | 79.44 | 84.04 |  |  | 57.3 | 40.1 | 53.5474 | 55.94 | 55.71 | 51.92 |  |  | 8.1 | 7.4 | 5.7329 | 17.18 | 9.41 | 9.82 | 6.0265 |  | 8.1 | 7.4 | 5.7329 | 17.24 | 9.47 | 9.83 |  |  | 8.1 | 7.4 | 5.7329 | 17.15 | 9.38 | 9.79 |  |  | 8.1 | 5.6 | 5.7329 | 17.16 | 9.39 | 9.53 |  |  | 8.1 | 7.4 | 5.7329 | 17.19 | 9.42 | 9.69 | 6.8571 |  | 8.1 | 7.4 | 5.7329 | 17.13 | 9.36 | 9.77 |  |  | 8.1 | 5.6 | 5.7329 | 17.08 | 9.31 | 9.45
| 12:00 | 72.5 | 79 | 60.158 | 66.07 | 65.84 | 71.8 | 54.7017 |  | 72.5 | 65.8 | 63.7872 | 75.82 | 75.6 | 75.32 |  |  | 69.1 | 64.8 | 64.2025 | 70.29 | 70.06 | 76.45 |  |  | 52.4 | 35 | 44.8893 | 47.84 | 47.61 | 44.87 |  |  | 77 | 77.4 | 62.3736 | 75.26 | 75.02 | 78.36 | 57.2128 |  | 69.5 | 70.5 | 59.7001 | 69.28 | 69.04 | 75.18 |  |  | 52.8 | 36.7 | 45.6465 | 45.83 | 45.59 | 42.27 |  |  | 7 | 6.3 | 4.0204 | 11.7 | 6.3 | 6.78 | 5.4777 |  | 7 | 6.3 | 4.0204 | 11.71 | 6.31 | 6.71 |  |  | 7 | 6.3 | 4.0204 | 11.69 | 6.29 | 6.76 |  |  | 7 | 4.5 | 4.0204 | 11.68 | 6.28 | 6.57 |  |  | 7 | 6.3 | 4.0204 | 11.73 | 6.32 | 6.69 | 6.3785 |  | 7 | 6.3 | 4.0204 | 11.68 | 6.28 | 6.74 |  |  | 7 | 4.5 | 4.0204 | 11.64 | 6.23 | 6.52
| 13:00 | 70.2 | 75.9 | 67.5631 | 69.19 | 68.98 | 77.77 | 45.2951 |  | 68.6 | 63.7 | 71.2331 | 78.14 | 77.93 | 82.11 |  |  | 71.8 | 68.4 | 74.3311 | 83.83 | 83.62 | 93.41 |  |  | 50.4 | 34.6 | 50.9932 | 50.89 | 50.67 | 50.97 |  |  | 75.1 | 75.2 | 69.4365 | 77.43 | 77.2 | 83.38 | 48.3642 |  | 72.2 | 73.5 | 69.6023 | 82.95 | 82.72 | 92.24 |  |  | 50.8 | 36.3 | 51.8636 | 49.07 | 48.84 | 48.5 |  |  | 6.8 | 6.1 | 5.6204 | 11.93 | 8.04 | 8.63 | 2.5344 |  | 6.8 | 6.1 | 5.6204 | 11.92 | 8.03 | 8.6 |  |  | 6.8 | 6.1 | 5.6204 | 11.92 | 8.03 | 8.62 |  |  | 6.8 | 4.5 | 5.6204 | 11.87 | 7.98 | 8.27 |  |  | 6.8 | 6.1 | 5.6204 | 11.99 | 8.1 | 8.5 | 5.0292 |  | 6.8 | 6.1 | 5.6204 | 11.91 | 8.02 | 8.6 |  |  | 6.8 | 4.5 | 5.6204 | 11.81 | 7.92 | 8.2
| 14:00 | 70.9 | 76.6 | 66.9351 | 67.96 | 67.71 | 77.57 | 52.566 |  | 69.5 | 66.5 | 70.4685 | 76.33 | 76.08 | 81.89 |  |  | 83.6 | 82.1 | 74.8515 | 94 | 93.76 | 103.32 |  |  | 51.3 | 37.7 | 50.6144 | 49.08 | 48.83 | 50.32 |  |  | 74.3 | 74.4 | 67.267 | 73.08 | 72.82 | 79.69 | 54.4815 |  | 84 | 86.6 | 69.7708 | 93.22 | 92.96 | 102.23 |  |  | 51.6 | 39.3 | 51.1924 | 47.39 | 47.13 | 47.93 |  |  | 7.8 | 7.2 | 5.8679 | 10.78 | 7.85 | 8.52 | 5.3379 |  | 7.8 | 7.2 | 5.8679 | 10.75 | 7.83 | 8.5 |  |  | 7.8 | 7.2 | 5.8679 | 10.84 | 7.92 | 8.46 |  |  | 7.8 | 5.6 | 5.8679 | 10.73 | 7.8 | 8.18 |  |  | 7.8 | 7.2 | 5.8679 | 10.84 | 7.92 | 8.39 | 5.2954 |  | 7.8 | 7.2 | 5.8679 | 10.83 | 7.91 | 8.44 |  |  | 7.8 | 5.6 | 5.8679 | 10.67 | 7.74 | 8.1
| 15:00 | 69.4 | 74.6 | 65.0993 | 65.42 | 65.19 | 75.71 | 52.689 |  | 68.1 | 66.2 | 68.6567 | 73.32 | 73.1 | 79.94 |  |  | 90.5 | 90.5 | 72.5138 | 94.2 | 93.97 | 103.88 |  |  | 50 | 37.7 | 49.4273 | 46.85 | 46.62 | 49.22 |  |  | 70.3 | 70.6 | 64.6127 | 67.01 | 66.77 | 73.9 | 52.4249 |  | 90.8 | 94.4 | 67.4199 | 93.5 | 93.27 | 102.86 |  |  | 50.2 | 39.2 | 49.815 | 45.29 | 45.05 | 46.92 |  |  | 8 | 7.3 | 5.8904 | 10.31 | 7.93 | 8.75 | 5.026 |  | 8 | 7.3 | 5.8904 | 10.27 | 7.9 | 8.73 |  |  | 8 | 7.3 | 5.8904 | 10.46 | 8.09 | 8.74 |  |  | 8 | 5.6 | 5.8904 | 10.25 | 7.87 | 8.39 |  |  | 8 | 7.3 | 5.8904 | 10.35 | 7.97 | 8.59 | 5.0552 |  | 8 | 7.3 | 5.8904 | 10.45 | 8.08 | 8.73 |  |  | 8 | 5.6 | 5.8904 | 10.19 | 7.81 | 8.32
| 16:00 | 67.3 | 72 | 61.7568 | 62.39 | 62.17 | 73.01 | 51.4478 |  | 65.9 | 65 | 65.5308 | 69.33 | 69.12 | 76.56 |  |  | 88.7 | 89.3 | 68.5476 | 85.95 | 85.74 | 95.49 |  |  | 48.5 | 37.7 | 47.3772 | 44.77 | 44.55 | 48.1 |  |  | 66.8 | 67.4 | 61.0573 | 62.29 | 62.07 | 71.04 | 50.1315 |  | 89.1 | 92.7 | 63.8459 | 85.33 | 85.11 | 94.53 |  |  | 48.7 | 39.1 | 47.7335 | 43.37 | 43.14 | 45.94 |  |  | 8.2 | 7.4 | 5.8679 | 9.76 | 7.82 | 8.67 | 4.979 |  | 8.2 | 7.4 | 5.8679 | 9.72 | 7.78 | 8.65 |  |  | 8.2 | 7.4 | 5.8679 | 9.95 | 8.01 | 8.7 |  |  | 8.2 | 5.6 | 5.8679 | 9.69 | 7.75 | 8.33 |  |  | 8.2 | 7.4 | 5.8679 | 9.77 | 7.83 | 8.62 | 4.9759 |  | 8.2 | 7.4 | 5.8679 | 9.94 | 8 | 8.69 |  |  | 8.2 | 5.6 | 5.8679 | 9.64 | 7.7 | 8.26
| 17:00 | 65 | 69.2 | 57.7217 | 58.55 | 58.36 | 69.22 | 49.2914 |  | 63.1 | 62.9 | 61.9469 | 63.8 | 63.61 | 71.19 |  |  | 78.8 | 78.9 | 62.8444 | 75.33 | 75.13 | 84.47 |  |  | 47.2 | 37.6 | 44.9204 | 42.85 | 42.66 | 47.02 |  |  | 64 | 64.4 | 57.2007 | 57.05 | 56.84 | 65.91 | 47.8574 |  | 79.3 | 81.9 | 58.6956 | 74.78 | 74.58 | 83.57 |  |  | 47.3 | 38.9 | 45.2712 | 41.62 | 41.41 | 45 |  |  | 8.2 | 7.4 | 6.0029 | 9.3 | 7.68 | 8.54 | 4.858 |  | 8.2 | 7.4 | 6.0029 | 9.27 | 7.65 | 8.51 |  |  | 8.2 | 7.4 | 6.0029 | 9.46 | 7.85 | 8.54 |  |  | 8.2 | 5.6 | 6.0029 | 9.24 | 7.62 | 8.22 |  |  | 8.2 | 7.4 | 6.0029 | 9.3 | 7.68 | 8.49 | 4.9076 |  | 8.2 | 7.4 | 6.0029 | 9.46 | 7.84 | 8.53 |  |  | 8.2 | 5.6 | 6.0029 | 9.19 | 7.57 | 8.16
| 18:00 | 59.9 | 63 | 51.7624 | 49.83 | 49.67 | 60.13 | 45.6696 |  | 58.1 | 57.9 | 55.9955 | 56.32 | 56.17 | 63.38 |  |  | 64.1 | 63.6 | 56.645 | 56.08 | 55.92 | 64.51 |  |  | 44.9 | 36.4 | 40.7939 | 39.02 | 38.86 | 43.66 |  |  | 59.1 | 58.9 | 51.0144 | 49.92 | 49.76 | 58.37 | 44.9205 |  | 64.7 | 66.1 | 52.9379 | 55.58 | 55.42 | 63.66 |  |  | 45 | 37.6 | 41.0518 | 37.94 | 37.77 | 41.78 |  |  | 6.8 | 6.1 | 3.9579 | 6.38 | 4.94 | 5.75 | 4.6217 |  | 6.8 | 6.1 | 3.9579 | 6.36 | 4.92 | 5.73 |  |  | 6.8 | 6.1 | 3.9579 | 6.44 | 5 | 5.74 |  |  | 6.8 | 4.2 | 3.9579 | 6.36 | 4.91 | 5.62 |  |  | 6.8 | 6.1 | 3.9579 | 6.38 | 4.93 | 5.72 | 4.7599 |  | 6.8 | 6.1 | 3.9579 | 6.44 | 4.99 | 5.73 |  |  | 6.8 | 4.2 | 3.9579 | 6.34 | 4.89 | 5.59
| 19:00 | 50.7 | 52.5 | 45.6059 | 39.76 | 39.64 | 47.59 | 40.1376 |  | 49.2 | 48.9 | 49.4668 | 46.13 | 46.01 | 51.14 |  |  | 51 | 50.4 | 50.058 | 44.86 | 44.74 | 51.93 |  |  | 39.3 | 31.7 | 35.3476 | 32.18 | 32.06 | 35.39 |  |  | 50.4 | 49.3 | 45.1367 | 40.13 | 40 | 46.45 | 39.7494 |  | 51.7 | 52.5 | 46.6178 | 44.42 | 44.29 | 51.12 |  |  | 39.5 | 32.8 | 35.4511 | 31.27 | 31.14 | 33.69 |  |  | 4.9 | 4.2 | 3.2704 | 4.99 | 3.72 | 4.47 | -1.5414 |  | 4.9 | 4.2 | 3.2704 | 4.98 | 3.71 | 4.47 |  |  | 4.9 | 4.2 | 3.2704 | 5 | 3.73 | 4.47 |  |  | 4.9 | 2.2 | 3.2704 | 4.98 | 3.71 | 4.42 |  |  | 4.9 | 4.2 | 3.2704 | 4.98 | 3.72 | 4.46 | 1.8037 |  | 4.9 | 4.2 | 3.2704 | 5 | 3.73 | 4.47 |  |  | 4.9 | 2.2 | 3.2704 | 4.97 | 3.7 | 4.4
| 20:00 | 44.1 | 45.3 | 41.3999 | 35.62 | 35.48 | 43.49 | 34.3065 |  | 42.6 | 42.6 | 45.0103 | 41.61 | 41.47 | 46.93 |  |  | 44.4 | 44.1 | 45.5404 | 40.2 | 40.06 | 47.6 |  |  | 34.3 | 27.4 | 32.2288 | 28.37 | 28.23 | 32.45 |  |  | 43.9 | 42.4 | 40.7444 | 35.96 | 35.81 | 42.51 | 33.9595 |  | 45.1 | 45.9 | 42.3174 | 39.8 | 39.66 | 46.83 |  |  | 34.4 | 28.4 | 32.2301 | 27.56 | 27.42 | 30.84 |  |  | 4.2 | 3.4 | 2.8704 | 4.43 | 3.24 | 4.02 | -4.07 |  | 4.2 | 3.4 | 2.8704 | 4.42 | 3.24 | 4.02 |  |  | 4.2 | 3.4 | 2.8704 | 4.43 | 3.25 | 4.02 |  |  | 4.2 | 1.4 | 2.8704 | 4.43 | 3.24 | 4.01 |  |  | 4.2 | 3.4 | 2.8704 | 4.43 | 3.24 | 4.02 | -3.24 |  | 4.2 | 3.4 | 2.8704 | 4.43 | 3.24 | 4.02 |  |  | 4.2 | 1.4 | 2.8704 | 4.42 | 3.23 | 4
| 21:00 | 40.3 | 38.9 | 29.0493 | 23.69 | 23.58 | 30.56 | 31.3713 |  | 38.8 | 36.9 | 32.1265 | 29.46 | 29.35 | 33.91 |  |  | 40.6 | 38.4 | 32.576 | 27.94 | 27.83 | 34.53 |  |  | 31.1 | 22.7 | 22.4585 | 17.72 | 17.6 | 20.97 |  |  | 40.1 | 36.4 | 27.9134 | 24.05 | 23.93 | 29.7 | 31.0885 |  | 41.3 | 39.9 | 29.7258 | 27.58 | 27.47 | 33.8 |  |  | 31.3 | 23.6 | 22.0379 | 16.91 | 16.79 | 19.44 |  |  | 4 | 2.6 | 1.8904 | 3.24 | 2.14 | 2.91 | -3.0021 |  | 4 | 2.6 | 1.8904 | 3.24 | 2.14 | 2.91 |  |  | 4 | 2.6 | 1.8904 | 3.24 | 2.14 | 2.91 |  |  | 4 | 0.6 | 1.8904 | 3.24 | 2.14 | 2.91 |  |  | 4 | 2.6 | 1.8904 | 3.24 | 2.14 | 2.91 | -1.9945 |  | 4 | 2.6 | 1.8904 | 3.24 | 2.14 | 2.91 |  |  | 4 | 0.6 | 1.8904 | 3.24 | 2.14 | 2.91
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
2017-11-11 | 0:00 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0
| 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 2:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 3:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 8:00 | -0.4 | 3 | 5.0438 | 3.11 | 4.06 | 8.79 | 10.9517 |  | 21.9 | 31.4 | 20.2118 | 37.62 | 38.6 | 47.89 |  |  | -3.3 | -0.5 | 4.409 | -0.81 | 0.15 | 4.42 |  |  | 13.2 | 21.6 | 13.4904 | 12.45 | 13.42 | 16.8 |  |  | 19.2 | 29.9 | 18.2983 | 33.22 | 34.2 | 41.43 | 45.188 |  | -1 | 2.9 | 10.7424 | 1.29 | 2.27 | 7.78 |  |  | 17.2 | 39.8 | 18.8737 | 15.28 | 16.28 | 20.85 |  |  | -3 | -0.6 | -2.4938 | -2.43 | -1.51 | -3.44 | -5.5633 |  | -3 | -0.7 | -2.4938 | -2.08 | -1.17 | -2.92 |  |  | -3 | -0.7 | -2.4938 | -2.52 | -1.6 | -3.55 |  |  | -3 | 0.5 | -2.4938 | -2.16 | -1.24 | -3.13 |  |  | -3 | -0.4 | -2.4938 | -2.1 | -1.18 | -2.95 | -0.67522 |  | -3 | -0.4 | -2.4938 | -2.4 | -1.49 | -3.34 |  |  | -3 | 0.7 | -2.4938 | -2.02 | -1.11 | -2.89
| 9:00 | 11 | 13.5 | 15.1078 | 11.38 | 11.99 | 17.31 | 24.6693 |  | 40 | 47.9 | 25.1894 | 41.53 | 42.16 | 53.1 |  |  | 9 | 12.4 | 15.2685 | 8.53 | 9.14 | 14.13 |  |  | 20.7 | 26.4 | 19.5976 | 17.99 | 18.62 | 21.8 |  |  | 42.3 | 48.9 | 32.7848 | 53 | 53.62 | 62.29 | 49.5882 |  | 10.1 | 13.1 | 22.748 | 9.48 | 10.1 | 15.66 |  |  | 23.5 | 28 | 26.8279 | 20.13 | 20.77 | 24.4 |  |  | 3.4 | 4.1 | 2.9424 | 1.51 | 2.8 | 2.33 | 2.2246 |  | 3.4 | 4.1 | 2.9424 | 1.71 | 3 | 2.72 |  |  | 3.4 | 4.1 | 2.9424 | 1.46 | 2.75 | 2.28 |  |  | 3.4 | 5.3 | 2.9424 | 1.63 | 2.91 | 2.45 |  |  | 3.4 | 4.2 | 2.9424 | 1.75 | 3.04 | 2.68 | 3.1123 |  | 3.4 | 4.2 | 2.9424 | 1.49 | 2.78 | 2.32 |  |  | 3.4 | 5.3 | 2.9424 | 1.66 | 2.95 | 2.5
| 10:00 | 13.1 | 15.7 | 15.501 | 13.79 | 14.35 | 19.27 | 25.8396 |  | 35 | 41.5 | 22.1332 | 30.63 | 31.2 | 42.93 |  |  | 11.1 | 14.6 | 15.9067 | 11.07 | 11.63 | 16.29 |  |  | 21.5 | 26.2 | 19.7815 | 19.31 | 19.87 | 22.86 |  |  | 53.6 | 61.1 | 37.5317 | 63.48 | 64.05 | 75.2 | 50.1932 |  | 12.1 | 15.3 | 25.554 | 11.92 | 12.48 | 17.66 |  |  | 24.2 | 27.8 | 29.1063 | 21.56 | 22.13 | 25.47 |  |  | 4 | 4.4 | 2.9199 | 2.13 | 3.08 | 2.64 | 2.1783 |  | 4 | 4.4 | 2.9199 | 2.3 | 3.26 | 3.02 |  |  | 4 | 4.4 | 2.9199 | 2.09 | 3.04 | 2.6 |  |  | 4 | 5.5 | 2.9199 | 2.23 | 3.18 | 2.72 |  |  | 4 | 4.4 | 2.9199 | 2.46 | 3.41 | 3.13 | 2.9703 |  | 4 | 4.4 | 2.9199 | 2.1 | 3.06 | 2.62 |  |  | 4 | 5.5 | 2.9199 | 2.26 | 3.21 | 2.76
| 11:00 | 14.5 | 17.2 | 15.7268 | 15.59 | 16.1 | 21.53 | 26.1233 |  | 23.9 | 28.2 | 19.805 | 17.77 | 18.29 | 27.78 |  |  | 12.6 | 16.2 | 16.3805 | 12.97 | 13.47 | 18.61 |  |  | 22 | 26.4 | 19.8334 | 20.15 | 20.67 | 23.48 |  |  | 60.5 | 68.3 | 41.3392 | 69.62 | 70.13 | 79.44 | 50.8958 |  | 13.5 | 16.8 | 27.7701 | 13.71 | 14.22 | 19.86 |  |  | 24.6 | 28.1 | 30.7713 | 22.25 | 22.77 | 25.91 |  |  | 4 | 4.5 | 2.9199 | 2.41 | 3.18 | 2.7 | 2.134 |  | 4 | 4.5 | 2.9199 | 2.5 | 3.27 | 2.95 |  |  | 4 | 4.5 | 2.9199 | 2.37 | 3.14 | 2.67 |  |  | 4 | 5.6 | 2.9199 | 2.5 | 3.27 | 2.8 |  |  | 4 | 4.5 | 2.9199 | 2.8 | 3.57 | 3.23 | 2.8436 |  | 4 | 4.5 | 2.9199 | 2.38 | 3.15 | 2.69 |  |  | 4 | 5.6 | 2.9199 | 2.53 | 3.3 | 2.84
| 12:00 | 12.8 | 15.1 | 8.5201 | 8.96 | 9.42 | 13.98 | 26.2586 |  | 15.1 | 17.5 | 12.0398 | 8.2 | 8.67 | 15.29 |  |  | 12.6 | 16.1 | 12.4266 | 11.15 | 11.6 | 16.88 |  |  | 19.8 | 23.5 | 13.498 | 13.58 | 14.05 | 15.51 |  |  | 61.8 | 68.8 | 35.5594 | 65.3 | 65.76 | 73.42 | 51.2449 |  | 13.4 | 16.7 | 24.6903 | 11.81 | 12.26 | 18.04 |  |  | 22.2 | 25.1 | 24.9659 | 15.52 | 15.99 | 17.79 |  |  | 2.9 | 3.4 | 1.1849 | 0.83 | 1.48 | 1.04 | 2.1373 |  | 2.9 | 3.4 | 1.1849 | 0.83 | 1.48 | 1.1 |  |  | 2.9 | 3.4 | 1.1849 | 0.81 | 1.45 | 1.02 |  |  | 2.9 | 4.5 | 1.1849 | 0.88 | 1.53 | 1.08 |  |  | 2.9 | 3.4 | 1.1849 | 1.09 | 1.74 | 1.35 | 2.7814 |  | 2.9 | 3.4 | 1.1849 | 0.81 | 1.46 | 1.03 |  |  | 2.9 | 4.5 | 1.1849 | 0.89 | 1.54 | 1.1
| 13:00 | 13.2 | 15.4 | 16.9612 | 16.06 | 16.49 | 22.1 | 18.1121 |  | 14.8 | 16.9 | 20.4665 | 14.91 | 15.35 | 23.22 |  |  | 22.4 | 27.3 | 25.3912 | 34.37 | 34.79 | 41.26 |  |  | 20 | 23.6 | 20.848 | 20.48 | 20.91 | 23.78 |  |  | 62 | 68.3 | 42.3982 | 69.25 | 69.68 | 78.04 | 51.1527 |  | 23.1 | 27.8 | 37.0036 | 34.95 | 35.38 | 42.33 |  |  | 22.3 | 25.1 | 32.197 | 22.27 | 22.71 | 25.89 |  |  | 2.8 | 3.3 | 2.7399 | 2.45 | 3.08 | 2.57 | 1.3341 |  | 2.8 | 3.3 | 2.7399 | 2.44 | 3.07 | 2.6 |  |  | 2.8 | 3.3 | 2.7399 | 2.44 | 3.07 | 2.61 |  |  | 2.8 | 4.5 | 2.7399 | 2.51 | 3.14 | 2.62 |  |  | 2.8 | 3.3 | 2.7399 | 2.91 | 3.54 | 3.11 | 2.2536 |  | 2.8 | 3.3 | 2.7399 | 2.45 | 3.08 | 2.62 |  |  | 2.8 | 4.5 | 2.7399 | 2.54 | 3.17 | 2.65
| 14:00 | 15.8 | 18.4 | 17.6749 | 16.5 | 16.91 | 21.71 | 25.8076 |  | 17.4 | 19.9 | 21.0055 | 15.12 | 15.54 | 22.65 |  |  | 39.5 | 46.4 | 28.5844 | 50.45 | 50.85 | 57.02 |  |  | 22.8 | 26.9 | 21.5831 | 21.51 | 21.92 | 24.49 |  |  | 60.6 | 66.3 | 38.2635 | 63.53 | 63.94 | 71.11 | 50.6184 |  | 39.9 | 46.8 | 38.4598 | 50.96 | 51.37 | 58.02 |  |  | 25 | 28.5 | 31.503 | 23.22 | 23.64 | 26.52 |  |  | 3.8 | 4.3 | 2.8299 | 2.53 | 3.13 | 2.61 | 1.7215 |  | 3.8 | 4.3 | 2.8299 | 2.51 | 3.11 | 2.63 |  |  | 3.8 | 4.3 | 2.8299 | 2.63 | 3.23 | 2.75 |  |  | 3.8 | 5.6 | 2.8299 | 2.61 | 3.21 | 2.68 |  |  | 3.8 | 4.3 | 2.8299 | 2.98 | 3.58 | 3.13 | 1.8863 |  | 3.8 | 4.3 | 2.8299 | 2.64 | 3.24 | 2.77 |  |  | 3.8 | 5.6 | 2.8299 | 2.64 | 3.23 | 2.71
| 15:00 | 15.3 | 17.6 | 17.0834 | 15.83 | 16.23 | 20.07 | 25.2633 |  | 16.8 | 19.1 | 20.4135 | 14.23 | 14.64 | 20.85 |  |  | 47.7 | 55.1 | 27.2297 | 56.39 | 56.79 | 62.31 |  |  | 23.1 | 27.3 | 21.3196 | 21.81 | 22.22 | 24.65 |  |  | 52.4 | 56.6 | 31.1476 | 51.24 | 51.64 | 57.48 | 50.4198 |  | 48.1 | 55.5 | 34.7401 | 56.85 | 57.25 | 63.25 |  |  | 25.2 | 28.8 | 29.0048 | 23.47 | 23.89 | 26.64 |  |  | 3.8 | 4.3 | 2.9199 | 2.72 | 3.25 | 2.75 | 1.7773 |  | 3.8 | 4.3 | 2.9199 | 2.69 | 3.22 | 2.76 |  |  | 3.8 | 4.3 | 2.9199 | 2.93 | 3.46 | 3.02 |  |  | 3.8 | 5.6 | 2.9199 | 2.8 | 3.34 | 2.83 |  |  | 3.8 | 4.3 | 2.9199 | 3.13 | 3.66 | 3.23 | 2.2585 |  | 3.8 | 4.3 | 2.9199 | 2.94 | 3.47 | 3.03 |  |  | 3.8 | 5.6 | 2.9199 | 2.82 | 3.36 | 2.86
| 16:00 | 14.3 | 16.2 | 14.7756 | 14.42 | 14.81 | 17.57 | 23.9027 |  | 15.5 | 17.5 | 18.2735 | 12.64 | 13.05 | 18.25 |  |  | 43.6 | 49.9 | 18.9529 | 46.89 | 47.29 | 51.64 |  |  | 23.3 | 27.6 | 19.9714 | 22.02 | 22.42 | 24.75 |  |  | 39.8 | 42 | 21.3941 | 35.37 | 35.77 | 40.13 | 44.1824 |  | 43.9 | 50.4 | 23.9353 | 47.3 | 47.7 | 52.52 |  |  | 25.3 | 29 | 25.003 | 23.66 | 24.06 | 26.72 |  |  | 4 | 4.4 | 3.0099 | 2.87 | 3.35 | 2.85 | 1.7701 |  | 4 | 4.4 | 3.0099 | 2.84 | 3.32 | 2.87 |  |  | 4 | 4.4 | 3.0099 | 3.15 | 3.62 | 3.2 |  |  | 4 | 5.6 | 3.0099 | 2.97 | 3.44 | 2.97 |  |  | 4 | 4.4 | 3.0099 | 3.2 | 3.68 | 3.26 | 2.2587 |  | 4 | 4.4 | 3.0099 | 3.15 | 3.63 | 3.21 |  |  | 4 | 5.6 | 3.0099 | 2.99 | 3.46 | 3
| 17:00 | 12.7 | 14.2 | 14.0716 | 12.32 | 12.72 | 14.52 | 22.4167 |  | 13.7 | 15.4 | 17.4269 | 10.42 | 10.83 | 15.12 |  |  | 25.9 | 29 | 17.7449 | 15.99 | 16.38 | 17.85 |  |  | 23.4 | 27.8 | 19.7426 | 22.12 | 22.52 | 24.79 |  |  | 27.3 | 27 | 19.3271 | 20.59 | 20.99 | 23.26 | 34.2869 |  | 26.3 | 29.4 | 22.1665 | 16.35 | 16.75 | 18.68 |  |  | 25.4 | 29.2 | 24.1732 | 23.75 | 24.16 | 26.74 |  |  | 4.1 | 4.5 | 3.0549 | 3.01 | 3.43 | 2.94 | 1.8235 |  | 4.1 | 4.5 | 3.0549 | 2.98 | 3.4 | 2.96 |  |  | 4.1 | 4.5 | 3.0549 | 3.26 | 3.68 | 3.28 |  |  | 4.1 | 5.6 | 3.0549 | 3.12 | 3.54 | 3.1 |  |  | 4.1 | 4.5 | 3.0549 | 3.23 | 3.66 | 3.25 | 2.1437 |  | 4.1 | 4.5 | 3.0549 | 3.26 | 3.69 | 3.29 |  |  | 4.1 | 5.6 | 3.0549 | 3.14 | 3.56 | 3.13
| 18:00 | 10.2 | 11.5 | 11.1631 | 9.28 | 9.69 | 10.56 | 22.0838 |  | 10.9 | 12.6 | 14.2427 | 7.1 | 7.52 | 10.93 |  |  | 12.3 | 13.5 | 14.5102 | 11.42 | 11.83 | 12.02 |  |  | 22.6 | 26.9 | 17.3696 | 19.83 | 20.24 | 22.18 |  |  | 20.3 | 18.7 | 15.6879 | 16.39 | 16.8 | 18.14 | 33.2965 |  | 12.8 | 13.8 | 18.7149 | 11.75 | 12.16 | 12.81 |  |  | 24.5 | 28.2 | 21.4248 | 21.47 | 21.88 | 24.15 |  |  | 2.8 | 3.2 | 1.0549 | 0.86 | 1.25 | 0.82 | 1.9298 |  | 2.8 | 3.2 | 1.0549 | 0.84 | 1.24 | 0.83 |  |  | 2.8 | 3.2 | 1.0549 | 0.89 | 1.28 | 0.86 |  |  | 2.8 | 4.2 | 1.0549 | 0.92 | 1.32 | 0.93 |  |  | 2.8 | 3.2 | 1.0549 | 0.92 | 1.32 | 0.89 | 2.3171 |  | 2.8 | 3.2 | 1.0549 | 0.89 | 1.28 | 0.86 |  |  | 2.8 | 4.2 | 1.0549 | 0.93 | 1.33 | 0.94
| 19:00 | 5.1 | 6.4 | 5.908 | 3.63 | 4.04 | 3.34 | 18.6745 |  | 5.4 | 7.3 | 8.6118 | 1.17 | 1.59 | 3.39 |  |  | 7 | 8.5 | 8.8371 | 5.05 | 5.45 | 4.02 |  |  | 18.4 | 22.5 | 12.8265 | 14.59 | 15.01 | 14.88 |  |  | 14.7 | 13.3 | 9.9193 | 9.95 | 10.36 | 10.22 | 29.4588 |  | 7.5 | 8.8 | 12.9371 | 5.34 | 5.75 | 4.77 |  |  | 20.3 | 23.7 | 16.4979 | 16.23 | 16.65 | 16.86 |  |  | 0.9 | 1.3 | 0.23236 | -0.02 | 0.37 | -0.04 | 1.5342 |  | 0.9 | 1.3 | 0.23236 | -0.03 | 0.36 | -0.03 |  |  | 0.9 | 1.3 | 0.23236 | -0.01 | 0.38 | -0.03 |  |  | 0.9 | 2.2 | 0.23236 | 0.02 | 0.41 | 0.03 |  |  | 0.9 | 1.3 | 0.23236 | 0.01 | 0.4 | -0.01 | 1.8963 |  | 0.9 | 1.3 | 0.23236 | -0.01 | 0.38 | -0.03 |  |  | 0.9 | 2.2 | 0.23236 | 0.02 | 0.41 | 0.04
| 20:00 | 1 | 2 | 3.267 | 0.92 | 1.32 | 1.08 | 13.2373 |  | 1 | 2.9 | 5.708 | -1.73 | -1.33 | 0.91 |  |  | 2.6 | 4.1 | 5.8845 | 1.86 | 2.26 | 1.37 |  |  | 14.6 | 18.5 | 10.6639 | 12.06 | 12.46 | 12.68 |  |  | 10 | 8.5 | 6.7508 | 6.61 | 7.01 | 7.46 | 23.7125 |  | 3.1 | 4.4 | 9.8582 | 2.13 | 2.52 | 2.09 |  |  | 16.5 | 19.7 | 14.0376 | 13.68 | 14.08 | 14.63 |  |  | 0 | 0.4 | -0.14514 | -0.49 | -0.1 | -0.48 | 0.89534 |  | 0 | 0.4 | -0.14514 | -0.5 | -0.11 | -0.48 |  |  | 0 | 0.4 | -0.14514 | -0.49 | -0.1 | -0.48 |  |  | 0 | 1.4 | -0.14514 | -0.46 | -0.07 | -0.45 |  |  | 0 | 0.4 | -0.14514 | -0.47 | -0.08 | -0.46 | 1.1802 |  | 0 | 0.4 | -0.14514 | -0.49 | -0.09 | -0.48 |  |  | 0 | 1.4 | -0.14514 | -0.46 | -0.07 | -0.44
| 21:00 | -1.3 | -1.6 | -7.3447 | -9.13 | -8.74 | -10.17 | 10.7304 |  | -1.5 | -1 | -5.4325 | -11.85 | -11.45 | -10.46 |  |  | 0 | 0.1 | -5.3214 | -8.52 | -8.12 | -10.08 |  |  | 12.6 | 14.1 | 1.862 | 2.61 | 3.01 | 1.97 |  |  | 7.2 | 4.4 | -4.5439 | -3.95 | -3.56 | -4.16 | 20.92 |  | 0.5 | 0.4 | -1.3049 | -8.28 | -7.88 | -9.4 |  |  | 14.5 | 15.2 | 4.6534 | 4.13 | 4.52 | 3.9 |  |  | -0.3 | -0.4 | -0.94514 | -1.33 | -0.95 | -1.31 | 0.49569 |  | -0.3 | -0.4 | -0.94514 | -1.33 | -0.95 | -1.31 |  |  | -0.3 | -0.4 | -0.94514 | -1.33 | -0.95 | -1.31 |  |  | -0.3 | 0.6 | -0.94514 | -1.33 | -0.95 | -1.31 |  |  | -0.3 | -0.4 | -0.94514 | -1.33 | -0.95 | -1.31 | 0.80125 |  | -0.3 | -0.4 | -0.94514 | -1.33 | -0.95 | -1.31 |  |  | -0.3 | 0.6 | -0.94514 | -1.33 | -0.95 | -1.31
| 22:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
| 24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図53 事務室1NP
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図54 事務室1NEP
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図55 事務室1NWP
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図56 事務室1NI
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図57 事務室2SP
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図58 事務室2SWP
(a) 1月4日
(b) 4月5日
(c) 7月18日
(d) 11月11日
図59 事務室2SI