## はじめに
Appendix C 冷却水サブシステムテスト結果入力ファイル
概要
このファイルは、6.3.5の冷却水サブシステムテストのシミュレーション結果を入力するファイルです。
このファイルは、他のツールによるシミュレーション結果と比較することが出来ます。
入力シート内の黄色セルにシミュレーション結果を入力することで、グラフシートに自動的に図が表示されます。
シートガイド
はじめに：本ファイルの使用方法
入力シート：ユーザーによるツールのシミュレーション結果を入力するシート
グラフシート：メーカ提供値および他のツールの計算結果を含むグラフを表示するシート
集計シート（非表示）：グラフ描画のためにデータを集計しているシート。「はじめに」などのシートタブを右クリック→再表示で表示可能
トライアル参加ツールの情報
| プログラム名 | バージョン情報 | 開発者 | 試行者※ | 特記事項
| HASP/ACSS |  | 一般社団法人建築設備技術者協会 | 委員A（ユーザー）
| LCEM |  | 国土交通省 営繕部 | 委員B（ユーザー）
| BEST |  | BESTコンソーシアム | 委員C（開発者）
| ACSES |  | 京都大学・岡山理科大学 吉田研究室 | 委員D（開発者）
| Popolo |  | 工学院大学 富樫研究室 | 委員E（開発者）
| ENe-ST | ― | 鹿島建設株式会社 | 委員F（開発者）
※委員（ユーザー）は本ガイドライン制定委員会の委員（開発者ではない）が一人のユーザーとしてトライアルを行ったことを示す。
一方、委員（開発者）は本ガイドライン制定委員会の委員かつ当該ツールの開発者（または開発チームの一人）がトライアルを行ったことを示す。
試行者は本ガイドラインで共通するアルファベットで匿名化されている。
2022年7月31日
公益社団法人空気調和・衛生工学会
空調システムのエネルギーシミュレーションツール評価法ガイドライン制定委員会

## 入力シート
計算結果入力シート
以下の黄色セルにツール名称等の基本情報および計算結果を入力してください。
入力するとグラフシートのグラフに計算結果が自動的に反映されます。
ツールの名称 | EnergyPlus
ツールのバージョン | Ver. 9.4
試行者 | 小野永吉
実施日 | 2022年3月17日
Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
| 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
| OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
| Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
| ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | ー | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 35.5841 | 2499.765 | 30.2077 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 30.2077 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4834 | -956.3097 | -956.3097 | 0 | 0.10696 | 18.6542 | 0.00022281
S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | ー | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 32.5397 | 2499.765 | 27.1625 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 27.1625 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3772 | 937.783 | 404.5306 | -6.8904 | -5.4863 | -956.8096 | -956.8096 | 0 | 0.1091 | 19.0268 | 0.00022726
S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | ー | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 29.5733 | 2499.765 | 24.196 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 24.196 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3773 | 937.8079 | 404.5306 | -6.9152 | -5.4881 | -957.1254 | -957.1254 | 0 | 0.11077 | 19.3177 | 0.00023074
S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | ー | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 27.3762 | 2499.765 | 10.9285 | 825.839 | 8.14 | 106981.2 | 1 | 1673.926 | 2499.765 | 22 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3762 | 937.6109 | 404.5306 | -6.7182 | -16.5336 | -952.6012 | -952.6012 | 0 | 0.085953 | 14.9905 | 0.00017905
S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | ー | 31.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.3765 | 2499.765 | 20.1509 | 788.7677 | 8.14 | 106981.2 | 1 | 1710.9973 | 2499.765 | 32 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -17.3115 | -952.6442 | -952.6442 | 0 | 0.085943 | 14.9887 | 0.00017903
S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | ー | 21.5 | 23.9149 | 3.8253 | 10.7439 | 7 | 1511.8281 | 30.2957 | 2499.765 | 26.2867 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 26.2867 | 16.63 |  | 2499.765 |  |  | 1.321 | 1.049 | 394.8938 | 4.009 | 699.1648 | 298.9368 | -5.3342 | -4.1186 | -718.2848 | -718.2848 | 0 | 0.10963 | 19.1203 | 0.00022838
S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | ー | 21.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 24.6678 | 2499.765 | 21.9434 | 2449.4153 | 8.14 | 106981.2 | 1 | 50.3497 | 2499.765 | 22 | 16.63 |  | 2499.765 |  |  | 1.3285 | 0.96721 | 263.4256 | 2.6678 | 465.2597 | 198.281 | -3.5531 | -2.8103 | -480.2514 | -480.2514 | 0 | 0.085962 | 14.9919 | 0.00017907
S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | ー | 21.5 | 11.3082 | 1.7888 | 8.7496 | 7 | 1511.8281 | 23.8832 | 2499.765 | 7.0455 | 290.8649 | 8.14 | 106981.2 | 1 | 2208.9001 | 2499.765 | 22 | 16.63 |  | 2499.765 |  |  | 1.3056 | 0.86496 | 184.5446 | 1.8832 | 328.4361 | 141.3523 | -2.5392 | -16.9237 | -343.4267 | -343.4267 | 0 | 0.085955 | 14.9908 | 0.00017906
S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | ー | 31.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 34.6679 | 2499.765 | 19.0359 | 437.967 | 8.14 | 106981.2 | 1 | 2061.798 | 2499.765 | 32 | 16.63 |  | 2499.765 |  |  | 1.3285 | 0.96721 | 263.4256 | 2.6679 | 465.282 | 198.281 | -3.5754 | -15.718 | -480.2705 | -480.2705 | 0 | 0.085943 | 14.9887 | 0.00017903
S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.2473 | 2499.765 | 31.9036 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 31.8709 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4538 | -951.1458 | -951.1458 | 0 | 0.11011 | 19.2033 | 5.7132
S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 34.3201 | 2499.765 | 28.9794 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 28.9434 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3767 | 937.7031 | 404.5306 | -6.8104 | -5.4523 | -950.8878 | -950.8878 | 0 | 0.11159 | 19.4621 | 6.2774
S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 31.4509 | 2499.765 | 26.1118 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 26.0735 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.0842 | 526.3621 | 5.3775 | 937.8319 | 404.5306 | -6.9392 | -5.4516 | -950.7677 | -950.7677 | 0 | 0.11256 | 19.6309 | 6.6951
S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 27.3762 | 2499.765 | 22 | 2499.765 | 3.2502 | 78777.3364 | 0.73637 | 0 | 2499.765 | 22 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.1146 | 526.3621 | 5.3762 | 937.6109 | 404.5306 | -6.7182 | -5.4622 | -952.6012 | -952.6012 | 0 | 0.085953 | 14.9905 | 0.00017905
S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.3765 | 2499.765 | 32 | 2499.765 | 1.4896 | 60737.4039 | 0.56774 | 0 | 2499.765 | 32 | 16.63 |  | 2499.765 |  |  | 1.3012 | 1.126 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4624 | -952.6442 | -952.6442 | 0 | 0.085943 | 14.9887 | 0.00017903
S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 23.9149 | 3.8253 | 10.7439 | 7 | 1511.8281 | 31.74 | 2499.765 | 27.7675 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 27.7313 | 16.63 |  | 2499.765 |  |  | 1.321 | 1.049 | 394.8938 | 4.0087 | 699.1165 | 298.9368 | -5.2859 | -4.084 | -712.249 | -712.249 | 0 | 0.11153 | 19.4516 | 6.3191
S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 25.7744 | 2499.765 | 23.1446 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 23.1064 | 16.63 |  | 2499.765 |  |  | 1.3285 | 0.96721 | 263.4256 | 2.6681 | 465.309 | 198.281 | -3.6024 | -2.7418 | -478.1756 | -478.1756 | 0 | 0.11198 | 19.5298 | 6.6632
S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 11.3082 | 1.7888 | 8.7496 | 7 | 1511.8281 | 23.8832 | 2499.765 | 22 | 2499.765 | 0.41418 | 36762.4614 | 0.34363 | 0 | 2499.765 | 22 | 16.63 |  | 2499.765 |  |  | 1.3056 | 0.95912 | 184.5446 | 1.8832 | 328.4361 | 141.3523 | -2.5392 | -1.9692 | -343.4267 | -343.4267 | 0 | 0.085955 | 14.9908 | 0.00017906
S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 34.6679 | 2499.765 | 32 | 2499.765 | 0.41587 | 36857.6911 | 0.34452 | 0 | 2499.765 | 32 | 16.63 |  | 2499.765 |  |  | 1.3285 | 1.0478 | 263.4256 | 2.6679 | 465.282 | 198.281 | -3.5754 | -2.7538 | -480.2705 | -480.2705 | 0 | 0.085943 | 14.9887 | 0.00017903
S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
→E+では冷却水ポンプ→冷却塔→ARの順なので別途計算した値を貼り付け（小野）

## グラフシート
QAS/メーカ値は作業中で参考値として表示しています（ARは特性テーブルからの推定値、その他はBESTの結果と同じ）
条件チェック
吸収式冷温水発生機 冷水入口温度
吸収式冷温水発生機 冷水出口温度
吸収式冷温水発生機 冷水流量
吸収式冷温水発生機 冷水処理熱量
計算結果
吸収式冷温水発生機 ガス消費量
吸収式冷温水発生機 電力消費量
吸収式冷温水発生機 冷却水入口水温＝冷却水ポンプ 出口水温
吸収式冷温水発生機 冷却水出口温度
吸収式冷温水発生機 冷却水放熱量
吸収式冷温水発生機 冷却水量
吸収式冷温水発生機 冷却水出入口温度差
吸収式冷温水発生機 COP
冷却塔 冷却水出口温度
冷却塔 冷却水出入口温度差
冷却塔 冷却水流量
冷却塔 ファン風量
冷却塔 ファンインバータ比
冷却塔 ファン消費電力
冷却塔 冷却水冷却熱量
三方弁 入口B流量
三方弁 出口流量
三方弁 混合後温度
三方弁 冷却水放熱量
冷却塔と三方弁 放熱量の差
冷却水ポンプ 消費電力
冷却水ポンプ 出口流量
冷却水ポンプ 揚程
冷却水ポンプインバータ比
冷却水ポンプ 出入口温度差
冷却水ポンプ 冷却水増加熱量
吸収式冷温水発生機 消費ガス熱量
吸収式冷温水発生機 排気ガス放熱量
冷却水回路の熱収支

## YourData
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | EnergyPlus | [5 empty] | 小野永吉
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2022年3月17日 |  | Modeler Organization for Tables and Charts (short): |  |  |  | 小野永吉
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | EnergyPlus
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2022年3月17日 |  | Model / Organization Indentifier for Charts (short): |  |  |  | EnergyPlus/小野永吉 | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | EnergyPlus
| Software: | EnergyPlus | [8 empty] | ツールのバージョン | Ver. 9.4
| Version: | Ver. 9.4 | [8 empty] | 試行者 | 小野永吉
| Date: | 2022年3月17日 | [8 empty] | 実施日 | 2022年3月17日
Last Hour of Simulation - Summary Outputs - 冷却水サブシステム
| Case No. | 境界条件、制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 35.5841 | 2499.765 | 30.2077 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 30.2077 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4834 | -956.3097 | -956.3097 | 0 | 0.10696 | 18.6542 | 0.00022281
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 32.5397 | 2499.765 | 27.1625 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 27.1625 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3772 | 937.783 | 404.5306 | -6.8904 | -5.4863 | -956.8096 | -956.8096 | 0 | 0.1091 | 19.0268 | 0.00022726
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 29.5733 | 2499.765 | 24.196 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 24.196 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3773 | 937.8079 | 404.5306 | -6.9152 | -5.4881 | -957.1254 | -957.1254 | 0 | 0.11077 | 19.3177 | 0.00023074
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 27.3762 | 2499.765 | 10.9285 | 825.839 | 8.14 | 106981.2 | 1 | 1673.926 | 2499.765 | 22 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3762 | 937.6109 | 404.5306 | -6.7182 | -16.5336 | -952.6012 | -952.6012 | 0 | 0.085953 | 14.9905 | 0.00017905
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.3765 | 2499.765 | 20.1509 | 788.7677 | 8.14 | 106981.2 | 1 | 1710.9973 | 2499.765 | 32 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -17.3115 | -952.6442 | -952.6442 | 0 | 0.085943 | 14.9887 | 0.00017903
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | 23.9149 | 3.8253 | 10.7439 | 7 | 1511.8281 | 30.2957 | 2499.765 | 26.2867 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 26.2867 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.321 | 1.049 | 394.8938 | 4.009 | 699.1648 | 298.9368 | -5.3342 | -4.1186 | -718.2848 | -718.2848 | 0 | 0.10963 | 19.1203 | 0.00022838
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 24.6678 | 2499.765 | 21.9434 | 2449.4153 | 8.14 | 106981.2 | 1 | 50.3497 | 2499.765 | 22 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3285 | 0.96721 | 263.4256 | 2.6678 | 465.2597 | 198.281 | -3.5531 | -2.8103 | -480.2514 | -480.2514 | 0 | 0.085962 | 14.9919 | 0.00017907
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | 11.3082 | 1.7888 | 8.7496 | 7 | 1511.8281 | 23.8832 | 2499.765 | 7.0455 | 290.8649 | 8.14 | 106981.2 | 1 | 2208.9001 | 2499.765 | 22 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3056 | 0.86496 | 184.5446 | 1.8832 | 328.4361 | 141.3523 | -2.5392 | -16.9237 | -343.4267 | -343.4267 | 0 | 0.085955 | 14.9908 | 0.00017906
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 34.6679 | 2499.765 | 19.0359 | 437.967 | 8.14 | 106981.2 | 1 | 2061.798 | 2499.765 | 32 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3285 | 0.96721 | 263.4256 | 2.6679 | 465.282 | 198.281 | -3.5754 | -15.718 | -480.2705 | -480.2705 | 0 | 0.085943 | 14.9887 | 0.00017903
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.2473 | 2499.765 | 31.9036 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 31.8709 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4538 | -951.1458 | -951.1458 | 0 | 0.11011 | 19.2033 | 5.7132
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 34.3201 | 2499.765 | 28.9794 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 28.9434 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3767 | 937.7031 | 404.5306 | -6.8104 | -5.4523 | -950.8878 | -950.8878 | 0 | 0.11159 | 19.4621 | 6.2774
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 31.4509 | 2499.765 | 26.1118 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 26.0735 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.0842 | 526.3621 | 5.3775 | 937.8319 | 404.5306 | -6.9392 | -5.4516 | -950.7677 | -950.7677 | 0 | 0.11256 | 19.6309 | 6.6951
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 27.3762 | 2499.765 | 22 | 2499.765 | 3.2502 | 78777.3364 | 0.73637 | 0 | 2499.765 | 22 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.1146 | 526.3621 | 5.3762 | 937.6109 | 404.5306 | -6.7182 | -5.4622 | -952.6012 | -952.6012 | 0 | 0.085953 | 14.9905 | 0.00017905
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.3624 | 5.0969 | 11.9903 | 7 | 1511.8281 | 37.3765 | 2499.765 | 32 | 2499.765 | 1.4896 | 60737.4039 | 0.56774 | 0 | 2499.765 | 32 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3012 | 1.126 | 526.3621 | 5.3765 | 937.6557 | 404.5306 | -6.763 | -5.4624 | -952.6442 | -952.6442 | 0 | 0.085943 | 14.9887 | 0.00017903
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 23.9149 | 3.8253 | 10.7439 | 7 | 1511.8281 | 31.74 | 2499.765 | 27.7675 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 27.7313 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.321 | 1.049 | 394.8938 | 4.0087 | 699.1165 | 298.9368 | -5.2859 | -4.084 | -712.249 | -712.249 | 0 | 0.11153 | 19.4516 | 6.3191
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 25.7744 | 2499.765 | 23.1446 | 2499.765 | 8.14 | 106981.2 | 1 | 0 | 2499.765 | 23.1064 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3285 | 0.96721 | 263.4256 | 2.6681 | 465.309 | 198.281 | -3.6024 | -2.7418 | -478.1756 | -478.1756 | 0 | 0.11198 | 19.5298 | 6.6632
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 11.3082 | 1.7888 | 8.7496 | 7 | 1511.8281 | 23.8832 | 2499.765 | 22 | 2499.765 | 0.41418 | 36762.4614 | 0.34363 | 0 | 2499.765 | 22 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3056 | 0.95912 | 184.5446 | 1.8832 | 328.4361 | 141.3523 | -2.5392 | -1.9692 | -343.4267 | -343.4267 | 0 | 0.085955 | 14.9908 | 0.00017906
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 15.8625 | 2.5527 | 9.4975 | 7 | 1511.8281 | 34.6679 | 2499.765 | 32 | 2499.765 | 0.41587 | 36857.6911 | 0.34452 | 0 | 2499.765 | 32 | 16.63 | 0 | 2499.765 | 0 | 0 | 1.3285 | 1.0478 | 263.4256 | 2.6679 | 465.282 | 198.281 | -3.5754 | -2.7538 | -480.2705 | -480.2705 | 0 | 0.085943 | 14.9887 | 0.00017903
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37 | 527.4423 | 32.4 |  | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.6 | 395.5817 | 22.1 |  | 2.9
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.4 | 263.7211 | 13.8 |  | 1.8
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.9 | 395.5817 | 22.6 |  | 2.9
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37 | 453.4887 | 28.6 |  | 5.1
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37 | 527.4423 | 31.3 |  | 5.1

## Aggregate Results
Output spreadsheet for Airside HVAC BESTEST
0
Aggregator Sheet - Collects data from Plots |  |  |  |  | S-CD100シリーズ | S-CD200シリーズ
AR_冷水処理熱量 | [kW] | Results Column ==> | 32 |  | AR_冷水処理熱量[kW] S-CD100シリーズ | AR_冷水処理熱量[kW] S-CD200シリーズ
OFFSETS
Cells B9:N9 contain the tab name of the results set. By changing the tab name all results for that column are changed and plot data updated. It is possible to change the order or plot multiple new results sets by changing the tab names. Plots currently only address through column J. To plot more than 9 results sets the plot ranges must be adjusted.
Tab Name==> | QAS | ENe-ST_小野 | LCEM_矢島 | BEST_二宮new | Popolo_富樫 | ACSESCX_吉田 | YourData | Blank | Blank | Blank | Blank | Blank | Blank |  | Summary Outputs | Detailed Outputs |  |  | Summary Output Columns | Detailed Output Columns
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD100 | 1 | #N/A | FC Heat | AE101: FC, Heating, OD/OWB = -29.00/-29.00 °C | OA_乾球温度 | Outdoor Air (oa)
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD101 | 2 | #N/A | FC Dry Coil | AE103: FC, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | OA_湿球温度 | Mixed Air (ma)
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD102 | 3 | #N/A | FC Wet Coil | AE104: FC, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | OA_相対湿度 | Heat Coil Outlet (hco)
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD103 | 4 | #N/A | SZ Heat | AE201: FC, Heating, -OD/OWB = 29.00/-29.00 °C | wcR_冷水定格流量比 | Cool Coil Outlet (cco)
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD104 | 5 | #N/A | SZ Dry Coil | AE203: SZ, Dry Coil Cooling, OD/OWB = 15.50/7.21 °C | wcR_冷水入口温度 | Supply Air (sa)
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 395.5817 | 395.5817 | 395.5817 | 395.5817 | 0 | 0 | 394.8938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD111 | 6 | #N/A | SZ Wet Coil | AE204: SZ, Wet Coil Cooling, OD/OWB = 26.90/23.44 °C | AR_冷水出口設定温度 | Zone Ar (z1)
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 263.7211 | 263.7211 | 263.7211 | 263.7211 | 0 | 0 | 263.4256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD112 | 7 | #N/A | SZ Dry Coil 2, No Econo | AE205: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, No Economizer | AR_冷却水設定温度差
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 184.6048 | 184.6048 | 184.6048 | 184.6048 | 0 | 0 | 184.5446 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD113 | 8 | #N/A | SZ Wet Coil 2, No Econo | AE206: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, No Economizer | 冷却塔ファン設定温度
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 263.7211 | 263.7211 | 263.7211 | 263.7211 | 0 | 0 | 263.4256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD114 | 9 | #N/A | SZ Dry Coil 2, Dry Bulb Econo | AE226: SZ, Wet Coil Cooling, OD/OWB = 23.00/21.53 °C, Dry Bulb Econo. | 三方弁設定温度
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD200 | 10 | #N/A | SZ Wet Coil 2, Enthalpy Econo | AE245: SZ, Dry Coil Cooling, OD/OWB = 24.90/13.03 °C, Enthalpy Econo | AR_ガス消費量
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD201 | 11 |  |  |  | AR_消費電力
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD202 | 12 |  |  |  | AR_冷水入口温度
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD203 | 13 |  |  |  | AR_冷水出口温度
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 527.4423 | 527.0063 | 527.4423 | 527.4423 | 0 | 0 | 526.3621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD204 | 14 |  |  |  | AR_冷水流量
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 395.5817 | 395.5817 | 395.5817 | 395.5817 | 0 | 0 | 394.8938 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD211 | 15 |  |  |  | AR_冷却水出口温度
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 263.7211 | 263.7211 | 263.7211 | 263.7211 | 0 | 0 | 263.4256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD212 | 16 |  |  |  | AR_冷却水流量
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 184.6048 | 184.6048 | 184.6048 | 184.6048 | 0 | 0 | 184.5446 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD213 | 17 |  |  |  | CT_冷却水出口温度
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 263.7211 | 263.7211 | 263.7211 | 263.7211 | 0 | 0 | 263.4256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD214 | 18 |  |  |  | CT_冷却水流量
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 263.7211 | 263.7211 | 263.7211 | 263.7211 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | S-CD215 | 19 |  |  |  | CT_ファン消費電力
CT_ファン風量
CT_ファンインバータ比
AR_ガス消費量 | [m3/h] | Results Column ==> | 10 |  | AR_ガス消費量[m3/h] S-CD100シリーズ | AR_ガス消費量[m3/h] S-CD200シリーズ | [12 empty] | V3W_入口B流量
Tab Name==> | [18 empty] | V3W_出口流量
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | [5 empty] | V3W_混合後温度
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 32.7815 | 32.3688 | 32.3824 | 32.4 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_消費電力
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 31.0816 | 30.7917 | 30.9137 | 31.3628 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_出口水温
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 29.7279 | 29.4763 | 29.6941 | 30.3673 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_出口流量
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 27.9871 | 28.0316 | 27.9962 | 28.7027 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_揚程
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 32.5001 | 32.294 | 32.1085 | 32.2508 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_INV比
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 22.3164 | 22.2107 | 22.3625 | 22.4359 | #N/A | #N/A | 23.9149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_COP
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 13.7967 | 13.7334 | 13.9719 | 14.0131 | #N/A | #N/A | 15.8625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | システム_COP
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 9.5061 | 9.5428 | 9.7765 | 9.8193 | #N/A | #N/A | 11.3082 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_冷水処理熱量
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 15.6679 | 15.6117 | 15.7341 | 15.3875 | #N/A | #N/A | 15.8625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_冷却水出入口温度差
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 32.7815 | 32.3693 | 32.3838 | 32.4 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_冷却水放熱量
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 31.0816 | 30.8 | 31.023 | 31.3628 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_消費ガス熱量
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 29.7279 | 29.4942 | 29.8244 | 30.3674 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | AR_排ガス放熱量
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 28.1341 | 28.264 | 28.3404 | 28.8712 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | CT_冷却水出入口温度差
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 32.8205 | 32.5785 | 32.4024 | 32.4 | #N/A | #N/A | 32.3624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | CT_冷却水冷却熱量
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 22.2117 | 22.3411 | 23.2889 | 22.6332 | #N/A | #N/A | 23.9149 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | V3W_冷却水放熱量
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 13.7051 | 14.0256 | 15.5699 | 14.4538 | #N/A | #N/A | 15.8625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | CTとV3W_冷却水放熱量の差
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 9.508 | 9.8209 | 10.8457 | 10.1948 | #N/A | #N/A | 11.3082 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_冷却水出入口温度差
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 15.6732 | 16.0614 | 17.3589 | 15.9479 | #N/A | #N/A | 15.8625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | PCD_冷却水増加熱量
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 13.7067 | 14.0256 | 15.5699 | 14.4539 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | [5 empty] | 冷却水回路の熱収支
AR_消費電力 | [kW] | Results Column ==> | 11 |  | AR_消費電力[kW] S-CD100シリーズ | AR_消費電力[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 5.0977 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 4.7383 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 4.4595 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 4.1107 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 5.0375 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 3.05 | 3.8 | 4.9723 | 4.1445 | #N/A | #N/A | 3.8253 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1.674 | 2.5333 | 4.8448 | 3.5687 | #N/A | #N/A | 2.5527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1.08 | 1.7733 | 4.7684 | 3.4073 | #N/A | #N/A | 1.7888 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1.9538 | 2.5333 | 4.8448 | 3.5687 | #N/A | #N/A | 2.5527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 5.0977 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 4.7383 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 4.4595 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 4.1397 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 5.1061 | 5.0625 | 5.0997 | 5.1 | #N/A | #N/A | 5.0969 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 3.0315 | 3.8 | 4.9723 | 4.1445 | #N/A | #N/A | 3.8253 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1.6606 | 2.5333 | 4.8448 | 3.5687 | #N/A | #N/A | 2.5527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1.0802 | 1.7733 | 4.7684 | 3.4073 | #N/A | #N/A | 1.7888 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1.9546 | 2.5333 | 4.8448 | 3.5687 | #N/A | #N/A | 2.5527 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1.6609 | 2.5333 | 4.8448 | 3.5687 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷水入口温度 | [℃] | Results Column ==> | 12 |  | AR_冷水入口温度[℃] S-CD100シリーズ | AR_冷水入口温度[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 10.75 | 10.75 | 10.75 | 10.75 | #N/A | #N/A | 10.7439 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 9.5 | 9.5 | 9.5 | 9.5 | #N/A | #N/A | 9.4975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 8.75 | 8.75 | 8.75 | 8.75 | #N/A | #N/A | 8.7496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 9.5 | 9.5 | 9.5 | 9.5 | #N/A | #N/A | 9.4975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 12 | 12 | 12 | 12 | #N/A | #N/A | 11.9903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 10.75 | 10.75 | 10.75 | 10.75 | #N/A | #N/A | 10.7439 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 9.5 | 9.5 | 9.5 | 9.5 | #N/A | #N/A | 9.4975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 8.75 | 8.75 | 8.75 | 8.75 | #N/A | #N/A | 8.7496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 9.5 | 9.5 | 9.5 | 9.5 | #N/A | #N/A | 9.4975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 9.5 | 9.5 | 9.5 | 9.5 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷水出口温度 | [℃] | Results Column ==> | 13 |  | AR_冷水出口温度[℃] S-CD100シリーズ | AR_冷水出口温度[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 7 | 7.0041 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 7 | 7 | 7 | 7 | #N/A | #N/A | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 7 | 7 | 7 | 7 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷水流量 | [L/min] | Results Column ==> | 14 |  | AR_冷水流量[L/min] S-CD100シリーズ | AR_冷水流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 1511.8281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1512 | 1512 | 1512 | 1512 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷却水出口温度 | [℃] | Results Column ==> | 15 |  | AR_冷却水出口温度[℃] S-CD100シリーズ | AR_冷却水出口温度[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 37.08 | 36.716 | 37 | 37.2 | #N/A | #N/A | 35.5841 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 34.13 | 33.545 | 34 | 34.27 | #N/A | #N/A | 32.5397 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 31.3 | 30.4744 | 31.2 | 31.46 | #N/A | #N/A | 29.5733 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 26.4 | 26.3155 | 26.2 | 26.47 | #N/A | #N/A | 27.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 36.62 | 36.5751 | 36.5 | 36.69 | #N/A | #N/A | 37.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 31.46 | 31.0852 | 31.5 | 31.61 | #N/A | #N/A | 30.2957 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 25.43 | 25.1099 | 25.5 | 25.61 | #N/A | #N/A | 24.6678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 23.21 | 23.2229 | 23.2 | 23.28 | #N/A | #N/A | 23.8832 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 34.02 | 34.0461 | 34 | 34.09 | #N/A | #N/A | 34.6679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 37.08 | 36.7195 | 37 | 37.2 | #N/A | #N/A | 37.2473 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 34.13 | 33.5951 | 34.3 | 34.27 | #N/A | #N/A | 34.3201 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 31.3 | 30.5625 | 31.5 | 31.46 | #N/A | #N/A | 31.4509 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 27 | 27.0891 | 27 | 27 | #N/A | #N/A | 27.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 37.13 | 37.1069 | 37 | 37.2 | #N/A | #N/A | 37.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 32.41 | 31.822 | 33 | 32.47 | #N/A | #N/A | 31.74 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 27.33 | 26.7742 | 28.5 | 27.4 | #N/A | #N/A | 25.7744 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 24.95 | 24.839 | 24.9 | 24.99 | #N/A | #N/A | 23.8832 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 36.5 | 36.5093 | 36.5 | 36.5 | #N/A | #N/A | 34.6679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 27.33 | 26.7742 | 28.5 | 27.4 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷却水流量 | [L/min] | Results Column ==> | 16 |  | AR_冷却水流量[L/min] S-CD100シリーズ | AR_冷却水流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2496.8163 | 2498.1921 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2451.4726 | 2444.2833 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 2499.9504 | 2411.5328 | 2412.0149 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 2453.6622 | 2373.8933 | 2330.8252 | 2488.7766 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2479.8717 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1871.9598 | 1817.5682 | 1840.6173 | 1894.104 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1275.474 | 1250 | 1290.8566 | 1286.7474 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_冷却水出口温度 | [℃] | Results Column ==> | 17 |  | CT_冷却水出口温度[℃] S-CD100シリーズ | CT_冷却水出口温度[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 31.94 | 31.6295 | 32.0008 | 32 | #N/A | #N/A | 30.2077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 29.07 | 28.5548 | 29.158 | 29.13 | #N/A | #N/A | 27.1625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 26.3 | 25.5645 | 26.4141 | 26.38 | #N/A | #N/A | 24.196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 17.78 | 14.1101 | 19.1321 | 17.95 | #N/A | #N/A | 10.9285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 24.57 | 22.5544 | 26.5004 | 24.67 | #N/A | #N/A | 20.1509 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 27.73 | 27.3724 | 27.9077 | 27.81 | #N/A | #N/A | 26.2867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 23 | 22.6708 | 23.1982 | 23.1 | #N/A | #N/A | 21.9434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 9.23 | 7.2588 | 15.0886 | 9.43 | #N/A | #N/A | 7.0455 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 20.66 | 19.4142 | 24.1065 | 20.76 | #N/A | #N/A | 19.0359 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 31.94 | 31.6268 | 31.9994 | 32 | #N/A | #N/A | 31.9036 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 29.07 | 28.5101 | 29.249 | 29.13 | #N/A | #N/A | 28.9794 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 26.3 | 25.4797 | 26.4823 | 26.38 | #N/A | #N/A | 26.1118 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 22 | 22.0047 | 21.9984 | 22 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 32 | 32.0076 | 31.9942 | 32 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 27.41 | 26.7729 | 27.9885 | 27.47 | #N/A | #N/A | 27.7675 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 22.42 | 22.005 | 23.5884 | 22.45 | #N/A | #N/A | 23.1446 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 16.71 | 12.9933 | 18.647 | 16.85 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 26.83 | 24.7726 | 27.7256 | 26.93 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 22.43 | 22.005 | 23.5884 | 22.45 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_冷却水流量 | [L/min] | Results Column ==> | 18 |  | CT_冷却水流量[L/min] S-CD100シリーズ | CT_冷却水流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1421.2392 | 987.7083 | 1662.4327 | 1457.8806 | #N/A | #N/A | 825.839 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1062.6252 | 906.2371 | 1250.0342 | 1080.4368 | #N/A | #N/A | 788.7677 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2449.4153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 305.496 | 270.6879 | 523.9642 | 321.063 | #N/A | #N/A | 290.8649 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 471.6174 | 436.4167 | 631.7216 | 486.1926 | #N/A | #N/A | 437.967 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2496.8163 | 2498.1921 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2451.4726 | 2444.2833 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 2499.9504 | 2411.5328 | 2412.0149 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 2453.6622 | 2373.8933 | 2330.8252 | 2488.7766 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2479.8717 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1871.9598 | 1817.5682 | 1840.6173 | 1894.104 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 523.5012 | 353.0027 | 679.6655 | 536.13 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 659.6436 | 534.4175 | 735.5695 | 672.1794 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_ファン消費電力 | [kW] | Results Column ==> | 19 |  | CT_ファン消費電力[kW] S-CD100シリーズ | CT_ファン消費電力[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 8.14 | 8.1522 | 8.1522 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1509 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1495 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 8.14 | 8.1522 | 8.1466 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 3.0933 | 2.1549 | 3.12 | 3.2294 | #N/A | #N/A | 3.2502 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1.1299 | 1.0715 | 0.8093 | 1.1712 | #N/A | #N/A | 1.4896 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 8.14 | 8.1522 | 8.1483 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 8.14 | 6.2764 | 8.1353 | 8.14 | #N/A | #N/A | 8.14 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.52096 | 0.52174 | 0.52174 | 0.52096 | #N/A | #N/A | 0.41418 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 0.52096 | 0.52174 | 0.52174 | 0.52096 | #N/A | #N/A | 0.41587 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 8.1343 | 6.2764 | 8.1353 | 8.1162 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_ファン風量 | [m3/h] | Results Column ==> | 20 |  | CT_ファン風量[m3/h] S-CD100シリーズ | CT_ファン風量[m3/h] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 106980 | 106980 | 106980 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106974.6 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106968.3 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 106980 | 106980 | 106955.5 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 77488.41 | 68657.5295 | 77671.6 | 78608.37 | #N/A | #N/A | 78777.3364 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 55391.22 | 54393.5295 | 49535.3 | 56058.63 | #N/A | #N/A | 60737.4039 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 106979.85 | 106980 | 106963 | 106979.79 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 106980 | 98049.9326 | 106906.3 | 106980 | #N/A | #N/A | 106981.2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 42792 | 42792 | 42792 | 42792 | #N/A | #N/A | 36762.4614 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 42792 | 42792 | 42792 | 42792 | #N/A | #N/A | 36857.6911 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 106954.86 | 98049.9326 | 106906.3 | 106875.69 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_ファンインバータ比 | [-] | Results Column ==> | 21 |  | CT_ファンインバータ比[-] S-CD100シリーズ | CT_ファンインバータ比[-] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 1 | 1 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 0.99995 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 0.99989 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1 | 1 | 0.99977 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 0.724 | 0.64178 | 0.72604 | 0.735 | #N/A | #N/A | 0.73637 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 0.518 | 0.50845 | 0.46303 | 0.524 | #N/A | #N/A | 0.56774 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1 | 1 | 0.99984 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1 | 0.91653 | 0.99931 | 1 | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.4 | 0.4 | 0.4 | 0.4 | #N/A | #N/A | 0.34363 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 0.4 | 0.4 | 0.4 | 0.4 | #N/A | #N/A | 0.34452 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 0.91653 | 0.99931 | 0.999 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
V3W_入口B流量 | [L/min] | Results Column ==> | 22 |  | V3W_入口B流量[L/min] S-CD100シリーズ | V3W_入口B流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1078.761 | 1512.2917 | 837.5655 | 1042.1196 | #N/A | #N/A | 1673.926 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1437.375 | 1593.7629 | 1249.964 | 1419.5634 | #N/A | #N/A | 1710.9973 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 0 | 0 | 0 | 0 | #N/A | #N/A | 50.3497 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 2194.5042 | 2229.3121 | 1976.0376 | 2178.9372 | #N/A | #N/A | 2208.9001 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 2028.3828 | 2063.5833 | 1868.2766 | 2013.8076 | #N/A | #N/A | 2061.798 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 727.4988 | 896.9973 | 570.3328 | 714.87 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 615.8304 | 715.5825 | 555.2854 | 614.568 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
V3W_出口流量 | [L/min] | Results Column ==> | 23 |  | V3W_出口流量[L/min] S-CD100シリーズ | V3W_出口流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2496.8163 | 2498.1921 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2451.4726 | 2444.2833 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 2499.9504 | 2411.5328 | 2412.0149 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 2453.6622 | 2373.8933 | 2330.8252 | 2488.7766 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2479.8717 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1871.9598 | 1817.5682 | 1840.6173 | 1894.104 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1275.474 | 1250 | 1290.8566 | 1286.7474 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
V3W_混合後温度 | [℃] | Results Column ==> | 24 |  | V3W_混合後温度[℃] S-CD100シリーズ | V3W_混合後温度[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 31.94 | 31.6295 | 32.0008 | 32 | #N/A | #N/A | 30.2077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 29.07 | 28.5548 | 29.158 | 29.13 | #N/A | #N/A | 27.1625 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 26.3 | 25.5645 | 26.4141 | 26.38 | #N/A | #N/A | 24.196 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 21.5 | 21.4938 | 21.5 | 21.5 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 31.5 | 31.4932 | 31.5 | 31.5 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 27.73 | 27.3724 | 27.9077 | 27.81 | #N/A | #N/A | 26.2867 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 23 | 22.6708 | 23.1982 | 23.1 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 21.5 | 21.4932 | 21.5 | 21.5 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 31.5 | 31.4923 | 31.5 | 31.5 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 31.94 | 31.6267 | 31.9994 | 32 | #N/A | #N/A | 31.8709 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 29.07 | 28.5101 | 29.249 | 29.13 | #N/A | #N/A | 28.9434 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 26.3 | 25.4797 | 26.4823 | 26.38 | #N/A | #N/A | 26.0735 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 22 | 22.0083 | 21.9984 | 22 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 32 | 32.0076 | 31.9942 | 32 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 27.41 | 26.773 | 27.9885 | 27.47 | #N/A | #N/A | 27.7313 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 22.42 | 22.005 | 23.5884 | 22.45 | #N/A | #N/A | 23.1064 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 21.5 | 21.4904 | 21.5 | 21.5 | #N/A | #N/A | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 31.5 | 31.4915 | 31.5 | 31.5 | #N/A | #N/A | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 22.43 | 22.005 | 23.5884 | 22.45 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_消費電力 | [kW] | Results Column ==> | 25 |  | PCD_消費電力[kW] S-CD100シリーズ | PCD_消費電力[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 16.1724 | 17.1008 | 16.6548 | 16.1724 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 16.4214 | 17.0728 | 16.5947 | 16.4214 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 16.4214 | 16.2798 | 15.6267 | 16.4214 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 16.4209 | 15.6304 | 15.0664 | 16.4214 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 15.9049 | 15.0473 | 13.7188 | 16.296 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 16.4214 | 17.1008 | 16.2612 | 16.4214 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 10.1498 | 8.018 | 7.3088 | 10.3444 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 5.4534 | 3.8406 | 2.8267 | 5.4534 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 5.4534 | 3.8406 | 2.8267 | 5.4534 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 5.6113 | 3.8406 | 3.0446 | 5.6848 | #N/A | #N/A | 16.63 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 5.4534 | 3.8406 | 2.8267 | 5.4534 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_出口水温 | [℃] | Results Column ==> | 26 |  | PCD_出口水温[℃] S-CD100シリーズ | PCD_出口水温[℃] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 31.95 | 31.718 | 32.0192 | 32.08 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 29.08 | 28.6433 | 29.1765 | 29.22 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 26.31 | 25.653 | 26.4326 | 26.46 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 21.51 | 21.5823 | 21.5184 | 21.58 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 31.51 | 31.5817 | 31.5184 | 31.58 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 27.74 | 27.4609 | 27.9261 | 27.89 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 23.01 | 22.7593 | 23.2166 | 23.19 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 21.51 | 21.5818 | 21.5184 | 21.58 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 31.51 | 31.5808 | 31.5184 | 31.58 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 31.95 | 31.7151 | 32.0179 | 32.08 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 29.08 | 28.5959 | 29.2668 | 29.22 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 26.31 | 25.5632 | 26.4996 | 26.46 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 22.01 | 22.0896 | 22.0144 | 22.08 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 32.01 | 32.0962 | 32.0121 | 32.08 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 27.43 | 26.8261 | 27.9996 | 27.54 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 22.43 | 22.0374 | 23.5947 | 22.5 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 21.51 | 21.5228 | 21.5063 | 21.55 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 31.51 | 31.5239 | 31.5065 | 31.55 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 22.43 | 22.0374 | 23.5947 | 22.5 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_出口流量 | [L/min] | Results Column ==> | 27 |  | PCD_出口流量[L/min] S-CD100シリーズ | PCD_出口流量[L/min] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2500 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2496.8163 | 2498.1921 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 2500.0002 | 2451.4726 | 2444.2833 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 2499.9504 | 2411.5328 | 2412.0149 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 2453.6622 | 2373.8933 | 2330.8252 | 2488.7766 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 2500.0002 | 2500 | 2479.8717 | 2500.0002 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1871.9598 | 1817.5682 | 1840.6173 | 1894.104 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1275.474 | 1250 | 1290.8566 | 1286.7474 | #N/A | #N/A | 2499.765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1251 | 1250 | 1250 | 1251 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_揚程 | [kPa] | Results Column ==> | 28 |  | PCD_揚程[kPa] S-CD100シリーズ | PCD_揚程[kPa] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 244.7305 | 244.6318 | 245.3962 | 244.7305 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 245 | 244.4547 | 244.6883 | 245 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 245 | 236.712 | 235.4971 | 245 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 244.9957 | 230.0132 | 230.0914 | 245 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 241.0038 | 223.7988 | 216.808 | 244.0321 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 245 | 244.6318 | 241.5423 | 245 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 190.8378 | 143.3618 | 146.268 | 192.7475 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 137.2862 | 83.3017 | 83.3 | 137.2862 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 137.2862 | 83.3017 | 83.3 | 137.2862 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 139.3969 | 83.3017 | 86.8811 | 140.3691 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 137.2862 | 83.3017 | 83.3 | 137.2862 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_INV比 | [-] | Results Column ==> | 29 |  | PCD_INV比[-] S-CD100シリーズ | PCD_INV比[-] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 0.99995 | 1 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1 | 0.99952 | 0.99861 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1 | 0.98341 | 0.97947 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1 | 0.96925 | 0.96804 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 0.991 | 0.95593 | 0.93934 | 0.997 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1 | 0.99995 | 0.9921 | 1 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 0.87 | 0.76278 | 0.76926 | 0.875 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 0.703 | 0.57791 | 0.57653 | 0.703 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.703 | 0.57791 | 0.57653 | 0.703 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 0.71 | 0.57791 | 0.58918 | 0.714 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0.703 | 0.57791 | 0.57653 | 0.703 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_COP | [-] | Results Column ==> | 30 |  | AR_COP[-] S-CD100シリーズ | AR_COP[-] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1.2872 | 1.3025 | 1.303 | 1.3023 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1.3576 | 1.3692 | 1.3649 | 1.3454 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1.4194 | 1.4303 | 1.421 | 1.3895 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1.5077 | 1.504 | 1.5072 | 1.4701 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1.2983 | 1.3055 | 1.3142 | 1.3084 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1.4181 | 1.4248 | 1.4152 | 1.4105 | #N/A | #N/A | 1.321 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1.5292 | 1.5362 | 1.51 | 1.5056 | #N/A | #N/A | 1.3285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1.5536 | 1.5476 | 1.5106 | 1.504 | #N/A | #N/A | 1.3056 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1.3466 | 1.3514 | 1.3409 | 1.3711 | #N/A | #N/A | 1.3285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1.2872 | 1.3025 | 1.303 | 1.3023 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1.3576 | 1.3688 | 1.3601 | 1.3454 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1.4194 | 1.4295 | 1.4148 | 1.3895 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 1.4998 | 1.4917 | 1.4889 | 1.4615 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1.2856 | 1.2941 | 1.3022 | 1.3023 | #N/A | #N/A | 1.3012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1.4248 | 1.4165 | 1.3589 | 1.3982 | #N/A | #N/A | 1.321 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1.5394 | 1.5042 | 1.355 | 1.4597 | #N/A | #N/A | 1.3285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1.5533 | 1.5038 | 1.3617 | 1.4486 | #N/A | #N/A | 1.3056 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1.3461 | 1.3136 | 1.2154 | 1.3229 | #N/A | #N/A | 1.3285 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1.5392 | 1.5042 | 1.355 | 1.4597 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
システム_COP | [-] | Results Column ==> | 31 |  | システム_COP[-] S-CD100シリーズ | システム_COP[-] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1.0775 | 1.0826 | 1.0856 | 1.0881 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1.1288 | 1.1283 | 1.1282 | 1.118 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1.1731 | 1.1695 | 1.1662 | 1.1483 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1.2355 | 1.2183 | 1.2237 | 1.2028 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1.0857 | 1.0847 | 1.0933 | 1.0923 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1.1202 | 1.1099 | 1.098 | 1.1062 | #N/A | #N/A | 1.049 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1.0857 | 1.0677 | 1.034 | 1.0517 | #N/A | #N/A | 0.96721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 0.98368 | 0.9587 | 0.91213 | 0.93286 | #N/A | #N/A | 0.86496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 0.9875 | 0.97502 | 0.95184 | 0.98428 | #N/A | #N/A | 0.96721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1.076 | 1.0828 | 1.0859 | 1.0866 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1.1271 | 1.1334 | 1.1317 | 1.1164 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1.1714 | 1.1793 | 1.1732 | 1.1466 | #N/A | #N/A | 1.0842 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 1.2728 | 1.274 | 1.2748 | 1.2333 | #N/A | #N/A | 1.1146 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1.1182 | 1.1208 | 1.134 | 1.1306 | #N/A | #N/A | 1.126 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 1.1793 | 1.1865 | 1.1417 | 1.1491 | #N/A | #N/A | 1.049 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 1.2401 | 1.2581 | 1.1105 | 1.1607 | #N/A | #N/A | 0.96721 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 1.338 | 1.3243 | 1.1715 | 1.2076 | #N/A | #N/A | 0.95912 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 1.2106 | 1.2017 | 1.0998 | 1.1677 | #N/A | #N/A | 1.0478 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 1.24 | 1.2581 | 1.1105 | 1.1611 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷却水出入口温度差 | [K] | Results Column ==> | 33 |  | AR_冷却水出入口温度差[K] S-CD100シリーズ | AR_冷却水出入口温度差[K] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 5.13 | 4.998 | 4.9808 | 5.12 | 0 | 0 | 5.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 5.05 | 4.9017 | 4.8235 | 5.05 | 0 | 0 | 5.3772 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 4.99 | 4.8213 | 4.7674 | 5 | 0 | 0 | 5.3773 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 4.89 | 4.7331 | 4.6816 | 4.89 | 0 | 0 | 5.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 5.11 | 4.9934 | 4.9816 | 5.11 | 0 | 0 | 5.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 3.72 | 3.6242 | 3.5739 | 3.72 | 0 | 0 | 4.009 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 2.42 | 2.3506 | 2.2834 | 2.42 | 0 | 0 | 2.6678 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1.7 | 1.6411 | 1.6816 | 1.7 | 0 | 0 | 1.8832 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 2.51 | 2.4653 | 2.4816 | 2.51 | 0 | 0 | 2.6679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 5.13 | 5.0044 | 4.9821 | 5.12 | 0 | 0 | 5.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 5.05 | 4.9992 | 5.0332 | 5.05 | 0 | 0 | 5.3767 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 4.99 | 4.9993 | 5.0004 | 5 | 0 | 0 | 5.3775 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 4.99 | 4.9995 | 4.9856 | 4.92 | 0 | 0 | 5.3762 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 5.12 | 5.0108 | 4.9879 | 5.12 | 0 | 0 | 5.3765 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 4.98 | 4.9959 | 5.0004 | 4.93 | 0 | 0 | 4.0087 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 4.9 | 4.7368 | 4.9053 | 4.9 | 0 | 0 | 2.6681 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 3.44 | 3.3161 | 3.3937 | 3.44 | 0 | 0 | 1.8832 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 4.99 | 4.9854 | 4.9935 | 4.95 | 0 | 0 | 2.6679 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 4.9 | 4.7368 | 4.9053 | 4.9 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_冷却水放熱量 | [kW] | Results Column ==> | 34 |  | AR_冷却水放熱量[kW] S-CD100シリーズ | AR_冷却水放熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 894.7683 | 871.7381 | 868.7383 | 893.0241 | 0 | 0 | 937.6557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 880.8148 | 854.9422 | 841.3128 | 880.8148 | 0 | 0 | 937.783 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 870.3496 | 840.9326 | 831.5274 | 872.0938 | 0 | 0 | 937.8079 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 852.9078 | 825.5465 | 816.5532 | 852.9078 | 0 | 0 | 937.6109 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 891.2799 | 870.9419 | 868.8788 | 891.2799 | 0 | 0 | 937.6557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 648.8378 | 632.1287 | 623.3494 | 648.8378 | 0 | 0 | 699.1648 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 422.0934 | 409.9839 | 398.265 | 422.0934 | 0 | 0 | 465.2597 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 296.5119 | 286.2372 | 293.2969 | 296.5119 | 0 | 0 | 328.4361 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 437.7911 | 429.9875 | 432.8319 | 437.7911 | 0 | 0 | 465.282 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 894.7683 | 871.7437 | 868.3516 | 893.0241 | 0 | 0 | 937.6557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 880.8148 | 855.0305 | 858.3151 | 880.8148 | 0 | 0 | 937.7031 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 870.3323 | 841.123 | 841.4613 | 872.0938 | 0 | 0 | 937.8319 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 854.2175 | 828.0218 | 810.7305 | 854.2877 | 0 | 0 | 937.6109 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 893.0241 | 873.971 | 862.9815 | 893.0241 | 0 | 0 | 937.6557 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 650.3977 | 633.5171 | 642.1246 | 651.4842 | 0 | 0 | 699.1165 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 427.6678 | 413.0958 | 427.7871 | 427.6678 | 0 | 0 | 465.309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 300.2403 | 289.1982 | 295.9662 | 300.2403 | 0 | 0 | 328.4361 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 444.0433 | 434.7766 | 449.7115 | 444.3771 | 0 | 0 | 465.282 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 427.6678 | 413.0958 | 427.7871 | 427.6678 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_消費ガス熱量 | [kW] | Results Column ==> | 35 |  | AR_消費ガス熱量[kW] S-CD100シリーズ | AR_消費ガス熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 409.7685 | 404.61 | 404.78 | 405 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 388.5199 | 384.8967 | 386.4206 | 392.0347 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 371.5988 | 368.4538 | 371.1759 | 379.5916 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 349.8393 | 350.3951 | 349.9526 | 358.7833 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 406.2511 | 403.6755 | 401.3562 | 403.1345 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 278.9554 | 277.634 | 279.5314 | 280.449 | 0 | 0 | 298.9368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 172.4582 | 171.6679 | 174.6489 | 175.1634 | 0 | 0 | 198.281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 118.8265 | 119.2854 | 122.2059 | 122.7409 | 0 | 0 | 141.3523 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 195.8488 | 195.1459 | 196.6765 | 192.344 | 0 | 0 | 198.281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 409.7685 | 404.6165 | 404.7974 | 405 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 388.5199 | 385.0004 | 387.7872 | 392.0355 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 371.5988 | 368.6772 | 372.8053 | 379.5924 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 351.6763 | 353.3004 | 354.2555 | 360.89 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 410.2557 | 407.2307 | 405.0301 | 405 | 0 | 0 | 404.5306 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 277.6458 | 279.2636 | 291.1116 | 282.9145 | 0 | 0 | 298.9368 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 171.314 | 175.3203 | 194.6237 | 180.6721 | 0 | 0 | 198.281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 118.8497 | 122.7607 | 135.5713 | 127.4352 | 0 | 0 | 141.3523 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 195.9149 | 200.7669 | 216.9861 | 199.349 | 0 | 0 | 198.281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 171.334 | 175.3203 | 194.6237 | 180.6742 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
AR_排ガス放熱量 | [kW] | Results Column ==> | 36 |  | AR_排ガス放熱量[kW] S-CD100シリーズ | AR_排ガス放熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 42.4425 | 59.8782 | 63.4841 | 39.4182 | 0 | 0 | -6.763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 35.1474 | 56.9608 | 72.5501 | 38.6622 | 0 | 0 | -6.8904 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 28.6915 | 54.5274 | 67.0909 | 34.9401 | 0 | 0 | -6.9152 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 24.3739 | 51.8549 | 60.8418 | 33.3178 | 0 | 0 | -6.7182 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 42.4135 | 59.7399 | 59.9197 | 39.297 | 0 | 0 | -6.763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 25.6993 | 41.087 | 51.7637 | 27.1929 | 0 | 0 | -5.3342 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 14.086 | 25.4051 | 40.105 | 16.7912 | 0 | 0 | -3.5531 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 6.9194 | 17.653 | 13.5138 | 10.8338 | 0 | 0 | -2.5392 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 21.7789 | 28.8796 | 27.5657 | 18.2741 | 0 | 0 | -3.5754 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 42.4425 | 59.8791 | 63.888 | 39.4182 | 0 | 0 | -6.763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 35.1474 | 56.9761 | 56.9144 | 38.6631 | 0 | 0 | -6.8104 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 28.7088 | 54.5605 | 58.7863 | 34.9409 | 0 | 0 | -6.9392 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 24.9011 | 52.2849 | 70.9673 | 34.0445 | 0 | 0 | -6.7182 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 44.6739 | 60.266 | 69.4909 | 39.4182 | 0 | 0 | -6.763 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 22.8298 | 41.3282 | 44.5687 | 27.012 | 0 | 0 | -5.2859 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 7.3673 | 25.9456 | 30.5578 | 16.7255 | 0 | 0 | -3.6024 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 3.2142 | 18.1673 | 24.2099 | 11.7998 | 0 | 0 | -2.5392 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 15.5928 | 29.7115 | 30.9957 | 18.693 | 0 | 0 | -3.5754 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 7.3873 | 25.9456 | 30.5578 | 16.7276 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_冷却水出入口温度差 | [kW] | Results Column ==> | 37 |  | CT_冷却水出入口温度差[kW] S-CD100シリーズ | CT_冷却水出入口温度差[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | -5.14 | -5.0865 | -4.9992 | -5.2 | 0 | 0 | -5.4834 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | -5.06 | -4.9902 | -4.842 | -5.14 | 0 | 0 | -5.4863 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | -5 | -4.9099 | -4.7859 | -5.08 | 0 | 0 | -5.4881 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | -8.62 | -12.2054 | -7.0679 | -8.52 | 0 | 0 | -16.5336 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | -12.05 | -14.0207 | -9.9996 | -12.02 | 0 | 0 | -17.3115 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | -3.73 | -3.7127 | -3.5923 | -3.8 | 0 | 0 | -4.1186 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | -2.43 | -2.4391 | -2.3018 | -2.51 | 0 | 0 | -2.8103 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | -13.98 | -15.964 | -8.1114 | -13.85 | 0 | 0 | -16.9237 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | -13.36 | -14.6319 | -9.8935 | -13.33 | 0 | 0 | -15.718 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | -5.14 | -5.0928 | -5.0006 | -5.2 | 0 | 0 | -5.4538 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | -5.06 | -5.085 | -5.051 | -5.14 | 0 | 0 | -5.4523 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | -5 | -5.0828 | -5.0177 | -5.08 | 0 | 0 | -5.4516 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | -5 | -5.0844 | -5.0016 | -5 | 0 | 0 | -5.4622 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | -5.13 | -5.0993 | -5.0058 | -5.2 | 0 | 0 | -5.4624 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | -5 | -5.0491 | -5.0115 | -5 | 0 | 0 | -4.084 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | -4.91 | -4.7692 | -4.9116 | -4.95 | 0 | 0 | -2.7418 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | -8.24 | -11.8457 | -6.253 | -8.14 | 0 | 0 | -1.9692 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | -9.67 | -11.7367 | -8.7744 | -9.57 | 0 | 0 | -2.7538 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | -4.9 | -4.7692 | -4.9116 | -4.95 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CT_冷却水冷却熱量 | [kW] | Results Column ==> | 38 |  | CT_冷却水冷却熱量[kW] S-CD100シリーズ | CT_冷却水冷却熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | -896.5124 | -887.1769 | -871.9532 | -906.9776 | 0 | 0 | -956.3097 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | -882.5589 | -870.381 | -844.5278 | -896.5124 | 0 | 0 | -956.8096 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | -872.0938 | -856.3715 | -834.7423 | -886.0473 | 0 | 0 | -957.1254 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | -854.7274 | -841.073 | -819.7632 | -866.5921 | 0 | 0 | -952.6012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | -893.3473 | -886.472 | -872.0871 | -906.0601 | 0 | 0 | -952.6442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | -650.582 | -647.5676 | -626.5643 | -662.7913 | 0 | 0 | -718.2848 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | -423.8376 | -425.4228 | -401.48 | -437.7911 | 0 | 0 | -480.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | -297.9654 | -301.4843 | -296.5172 | -310.2367 | 0 | 0 | -343.4267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | -439.5917 | -445.5084 | -436.0406 | -452.1595 | 0 | 0 | -480.2705 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | -896.5124 | -887.1403 | -871.5718 | -906.9776 | 0 | 0 | -951.1458 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | -882.5589 | -869.7024 | -861.3491 | -896.5124 | 0 | 0 | -950.8878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | -872.0764 | -855.1596 | -844.3875 | -886.0473 | 0 | 0 | -950.7677 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | -855.9294 | -842.0786 | -813.3388 | -868.1786 | 0 | 0 | -952.6012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | -894.7683 | -889.4098 | -866.0702 | -906.9776 | 0 | 0 | -952.6442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | -653.0098 | -640.2607 | -643.547 | -660.7345 | 0 | 0 | -712.249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | -428.5406 | -415.9219 | -428.3392 | -432.0318 | 0 | 0 | -478.1756 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | -300.9526 | -291.7375 | -296.5077 | -304.4722 | 0 | 0 | -343.4267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | -445.0297 | -437.6027 | -450.2937 | -448.7974 | 0 | 0 | -480.2705 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | -427.6678 | -415.9219 | -428.3392 | -432.0318 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
V3W_冷却水放熱量 | [kW] | Results Column ==> | 39 |  | V3W_冷却水放熱量[kW] S-CD100シリーズ | V3W_冷却水放熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | -896.5124 | -887.1769 | -871.9532 | -906.9776 | 0 | 0 | -956.3097 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | -882.5589 | -870.381 | -844.5278 | -896.5124 | 0 | 0 | -956.8096 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | -872.0938 | -856.3715 | -834.7423 | -886.0473 | 0 | 0 | -957.1254 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | -854.6519 | -840.9853 | -819.7681 | -866.8613 | 0 | 0 | -952.6012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | -893.0241 | -886.3807 | -872.0938 | -905.2334 | 0 | 0 | -952.6442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | -650.582 | -647.5676 | -626.5643 | -662.7913 | 0 | 0 | -718.2848 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | -423.8376 | -425.4228 | -401.48 | -437.7911 | 0 | 0 | -480.2514 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | -298.2561 | -301.676 | -296.5119 | -310.4654 | 0 | 0 | -343.4267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | -439.5353 | -445.4263 | -436.0469 | -451.7446 | 0 | 0 | -480.2705 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | -896.5124 | -887.1577 | -871.5718 | -906.9776 | 0 | 0 | -951.1458 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | -882.5589 | -869.6992 | -861.3491 | -896.5124 | 0 | 0 | -950.8878 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | -872.0764 | -855.1568 | -844.3875 | -886.0473 | 0 | 0 | -950.7677 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | -855.9294 | -841.4751 | -813.3388 | -868.1786 | 0 | 0 | -952.6012 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | -894.7683 | -889.4098 | -866.0702 | -906.9776 | 0 | 0 | -952.6442 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | -653.0098 | -640.2463 | -643.547 | -660.7345 | 0 | 0 | -712.249 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | -428.5406 | -415.9219 | -428.3392 | -432.0318 | 0 | 0 | -478.1756 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | -301.113 | -292.0243 | -296.5119 | -304.6042 | 0 | 0 | -343.4267 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | -444.9332 | -437.6027 | -450.2992 | -448.8657 | 0 | 0 | -480.2705 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | -427.6678 | -415.9219 | -428.3392 | -432.0318 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CTとV3W_冷却水放熱量の差 | [kW] | Results Column ==> | 40 |  | CTとV3W_冷却水放熱量の差[kW] S-CD100シリーズ | CTとV3W_冷却水放熱量の差[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | -0.075413 | -0.087683 | 0.0048991 | 0.26918 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | -0.32321 | -0.091243 | 0.0066865 | -0.8267 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 0.29067 | 0.19168 | -0.0052805 | 0.22868 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | -0.056369 | -0.082161 | 0.0063108 | -0.4149 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 0 | 0.017348 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 0 | -0.0032177 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 0 | -0.0027772 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 0 | -0.60353 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 3.2336e-08 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 0 | -0.014445 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.16047 | 0.28688 | 0.0041528 | 0.13199 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | -0.096531 | -5.6843e-12 | 0.005531 | 0.068382 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_冷却水出入口温度差 | [kW] | Results Column ==> | 41 |  | PCD_冷却水出入口温度差[kW] S-CD100シリーズ | PCD_冷却水出入口温度差[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.10696 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.088516 | 0.018432 | 0.09 | 0 | 0 | 0.1091 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.11077 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.085953 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.085943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.10963 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 0.01 | 0.088516 | 0.018432 | 0.09 | 0 | 0 | 0.085962 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.085955 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.088516 | 0.018432 | 0.08 | 0 | 0 | 0.085943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.088486 | 0.018476 | 0.08 | 0 | 0 | 0.11011 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.085765 | 0.017791 | 0.09 | 0 | 0 | 0.11159 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 0.01 | 0.083412 | 0.017389 | 0.08 | 0 | 0 | 0.11256 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.081229 | 0.01604 | 0.08 | 0 | 0 | 0.085953 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.088516 | 0.017852 | 0.08 | 0 | 0 | 0.085943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 0.02 | 0.053066 | 0.011077 | 0.07 | 0 | 0 | 0.11153 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 0.01 | 0.032406 | 0.006331 | 0.05 | 0 | 0 | 0.11198 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.032406 | 0.0062569 | 0.05 | 0 | 0 | 0.085955 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 0.01 | 0.032406 | 0.0065259 | 0.05 | 0 | 0 | 0.085943 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 0.032406 | 0.006331 | 0.05 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PCD_冷却水増加熱量 | [kW] | Results Column ==> | 42 |  | PCD_冷却水増加熱量[kW] S-CD100シリーズ | PCD_冷却水増加熱量[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 18.6542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 15.4388 | 3.215 | 15.6977 | 0 | 0 | 19.0268 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 19.3177 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 14.9905 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 14.9887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 19.1203 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1.7442 | 15.4388 | 3.215 | 15.6977 | 0 | 0 | 14.9919 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 14.9908 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | 1.7442 | 15.4388 | 3.215 | 13.9535 | 0 | 0 | 14.9887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 15.414 | 3.2202 | 13.9535 | 0 | 0 | 19.2033 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 14.6687 | 3.034 | 15.6977 | 0 | 0 | 19.4621 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 1.7442 | 14.0338 | 2.9262 | 13.9535 | 0 | 0 | 19.6309 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | 1.7119 | 13.4533 | 2.6083 | 13.8909 | 0 | 0 | 14.9905 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1.7442 | 15.4388 | 3.0887 | 13.9535 | 0 | 0 | 14.9887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | 2.612 | 6.7291 | 1.4224 | 9.2503 | 0 | 0 | 19.4516 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | 0.87279 | 2.8261 | 0.55213 | 4.364 | 0 | 0 | 19.5298 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.87279 | 2.8261 | 0.54566 | 4.364 | 0 | 0 | 14.9908 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | 0.88987 | 2.8261 | 0.58772 | 4.4887 | 0 | 0 | 14.9887 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 2.8261 | 0.55213 | 4.364 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
冷却水回路の熱収支 | [kW] | Results Column ==> | 43 |  | 冷却水回路の熱収支[kW] S-CD100シリーズ | 冷却水回路の熱収支[kW] S-CD200シリーズ
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | 2.5024e-13 | 9.0594e-14 | 4.8406e-14 | 4.7962e-14 | 0 | 0 | 0.00022281 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | -9.0816e-14 | -1.3678e-13 | -6.5281e-14 | 0 | 0 | 0 | 0.00022726 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | 2.2871e-14 | -3.1974e-14 | -6.5281e-14 | -1.4211e-14 | 0 | 0 | 0.00023074 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | -0.075413 | -0.087683 | 0.0048991 | 0.26918 | 0 | 0 | 0.00017905 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | -0.32321 | -0.091243 | 0.0066865 | -0.8267 | 0 | 0 | 0.00017903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | -9.0816e-14 | 2.1316e-14 | 4.8406e-14 | 9.9476e-14 | 0 | 0 | 0.00022838 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD112 WB19 CWSP21.5/6 FanSP22 Load50 | 1.7319e-14 | -2.3093e-14 | -8.4377e-15 | 0 | 0 | 0 | 0.00017907 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD113 WB7 CWSP21.5/5 FanSP32 Load100 | 0.29067 | 0.19168 | -0.0052805 | 0.22868 | 0 | 0 | 0.00017906 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD114 WB27 CWSP21.5/5 FanSP32 Load100 | -0.056369 | -0.082161 | 0.0063108 | -0.4149 | 0 | 0 | 0.00017903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD200 WB27 CWSP21.5/5 FanSP22 Load100 | 2.5024e-13 | 0.017348 | -7.1498e-14 | 4.7962e-14 | 0 | 0 | 5.7132 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD201 WB23 CWSP21.5/5 FanSP22 Load100 | -9.0816e-14 | -0.0032177 | -2.7978e-14 | 0 | 0 | 0 | 6.2774 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD202 WB19 CWSP21.5/5 FanSP22 Load100 | 8.8818e-15 | -0.0027772 | -1.6875e-14 | -1.4211e-14 | 0 | 0 | 6.6951 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD203 WB7 CWSP21.5/5 FanSP32 Load100 | -1.3101e-14 | -0.60353 | -1.1546e-14 | -2.1316e-13 | 0 | 0 | 0.00017905 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD204 WB27 CWSP21.5/5 FanSP32 Load100 | 1.3656e-13 | 3.2336e-08 | -8.8818e-14 | 4.7962e-14 | 0 | 0 | 0.00017903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD211 WB23 CWSP21.5/5 FanSP22 Load75 | -1.1546e-14 | -0.014445 | -9.0594e-14 | -7.4607e-14 | 0 | 0 | 6.3191 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | -5.7732e-15 | 3.8192e-14 | 8.9373e-14 | -6.4837e-14 | 0 | 0 | 6.6632 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | 0.16047 | 0.28688 | 0.0041528 | 0.13199 | 0 | 0 | 0.00017906 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | -0.096531 | -5.7065e-12 | 0.005531 | 0.068382 | 0 | 0 | 0.00017903 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | 0 | 3.8192e-14 | 8.9373e-14 | -6.4837e-14 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Detailed Outputs
Outdoor Air Temp |  | Results Column ==> | 1 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Temperature (just for 5 cases)
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio |  | Results Column ==> | 1 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Humidity Ratio (just for 5 cases)
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Outdoor Air Mass Flow Rat |  | Results Column ==> | 1 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Cooling Coil Outlet Air Temperature |  | Results Column ==> | 4 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Temperature |  | Results Column ==> | 5 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Humidity Ratio |  | Results Column ==> | 5 |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Specific Volume |  | Results Column ==> | 5 |  | Results Row Offset==> | 2
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Enthalpy |  | Results Column ==> | 5 |  | Results Row Offset==> | 3
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Air Mass Flow Rate |  | Results Column ==> | 5 |  | Results Row Offset==> | 4
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Air Temperature |  | Results Column ==> | 6 |  | Results Row Offset==> | 0
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Supply Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Return Fan Temperature Rise (°C)
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio Rise (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Humidity Ratio (gw/gda) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone Latent Gain (gw/s) |  |  |  |  | Results Row Offset==> | 1
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
S-CD100 WB27 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD101 WB23 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD102 WB19 CWSP21.5/5 FanSP22 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD103 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD104 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD111 WB23 CWSP21.5/5 FanSP22 Load75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD212 WB19 CWSP21.5/6 FanSP22 Load50 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD213 WB7 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD214 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
S-CD215 WB27 CWSP21.5/5 FanSP32 Load100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Delta Results
Output spreadsheet for SHASE冷却水サブシステムテスト
Aggregator Sheet - DELTA RESULTS for Delta Plots
AR冷却水出入口温度差
Tab Name==>
Cases | QAS | ENe-ST_小野 | LCEM_矢島 | BEST_二宮new | Popolo_富樫 | ACSESCX_吉田 | YourData | Blank | Blank | Blank | Blank | Blank | Blank
| QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
AE201-AE101 Heating -29.0/-29.0 | -0.059605 | -0.064549 | -0.067382 | -0.058321 | -0.066421 | -0.067 | -0.070108 | -0.059584 | -0.04118 | #N/A | #N/A | #N/A | #N/A
AE203-AE103 Dry Coil Cooling 15.5/-3.0 | 0.072652 | 0.068956 | 0.067631 | 0.063303 | 0.067154 | 0.068 | 0.067746 | 0.072468 | 0.04094 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Total Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06085 | 0.17848 | 0.066443 | 0.068 | 0.067691 | 0.077318 | 0.01169 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Sensible Coil Load 26.9/22.1 | 0.077372 | 0.07042 | 0.06503 | 0.069165 | 0.067164 | 0.067 | 0.066631 | 0.077323 | 0.0217 | #N/A | #N/A | #N/A | #N/A
AE204-AE104 Wet Coil Cooling Latent Coil Load 26.9/22.1 | 0 | -5.7732e-15 | -0.0041804 | 0.10932 | -0.00072059 | 0.001 | 0.0010596 | -5.7975e-06 | -0.01001 | #N/A | #N/A | #N/A | #N/A
Economizer
Tab Name==>
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29113 | 0.29622 | 0.27691 | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | 0.2914 | 0.29211 | 0.28703 | 0.2793 | 0.29465 | 0.295 | 0.29161 | 0.29622 | 0.27708 | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0 | 0 | 0 | 0 | 0 | 0 | -0.00047276 | 0 | -0.00017 | #N/A | #N/A | #N/A | #N/A
Total Cooling | 0.68493 | 0.67125 | 0.82473 | 0.67348 | 0.67988 | 0.681 | 0.69228 | 0.68443 | 0.59689 | #N/A | #N/A | #N/A | #N/A
Sensible Cooling | -0.14458 | -0.14373 | -0.13841 | -0.12602 | -0.14185 | -0.143 | -0.14226 | -0.143 | -0.1168 | #N/A | #N/A | #N/A | #N/A
Latent Cooling | 0.82951 | 0.81497 | 0.96314 | 0.7995 | 0.82172 | 0.825 | 0.83454 | 0.82743 | 0.71369 | #N/A | #N/A | #N/A | #N/A
Temperature
DB | AE101 | AE102 | AE103 | AE104 | AE105 | AE106
Original DB | -20 | 30 | 60 | 80 | 77 | 74
New DB | -20.2 | 30.02 | 59.9 | 80.42 | 76.82 | 73.4
Original WB | -20 | 20 | 45 | 75 | 55 | 70
New WB | -20.2 | 19.756 | 44.972 | 74.191 | 55.452 | 70.744
Outdoor Air Fraction
Cases | QAS/メーカ値 | ENe-ST/小野永吉 | LCEM/Yajima | BEST2108dev/nino | Popolo_富樫 | ACSESCX_吉田 | EnergyPlus/小野永吉 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
AE101 FC Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.34223 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE103 FC Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE104 FC Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33353 | 0.32295 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE201 SZ Heat -29.0/-29.0 | 0.34224 | 0.34226 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.34223 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE203 SZ Dry Coil 15.5/-3.0 | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE204 SZ Wet Coil 26.9/22.1 | 0.32294 | 0.32294 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32295 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE205 SZ Dry Coil 24.9/2.4 No Econo | 0.32755 | 0.32755 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32756 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE206 SZ Wet Coil 23.0/20.9 No Econo | 0.32756 | 0.32756 | 0.33333 | 0.33333 | 0.33333 | 0.33334 | 0.33333 | 0.32757 | 0.33334 | #N/A | #N/A | #N/A | #N/A
AE226 SZ Wet Coil 23.0/20.9 Dry Bulb Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99876 | #N/A | #N/A | #N/A | #N/A
AE245 SZ Dry Coil 24.9/2.4 Enthalpy Econo | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.92257 | #N/A | #N/A | #N/A | #N/A
|  | Original Case Conditions |  | New Case Conditions |  | June 13th 2012 case conditions
| Case | DB (°F) | WB (°F) | DB (°F) | WB (°F) | DB (°C) | WB (°C)
| AE101 | -20 | -20 | -20.2 | -20.2 | -29 | -29
| AE102 | 30 | 20 | 30.02 | 19.756
| AE103 | 60 | 45 | 59.9 | 44.972 | 15.5 | 7.2
| AE104 | 80 | 75 | 80.42 | 74.191 | 26.9 | 23.4
| AE105 | 77 | 55 | 76.82 | 55.452 | 24.9 | 13.03
| AE106 | 74 | 70 | 73.4 | 70.744 | 23 | 21.5

## QAS
Sec5-5out.XLS
Output spreadsheet for Standard 140 Air Handler Simulation Trail
INSTRUCTIONS |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
|  |  |  | Quasi-analytic Solution V1 | [5 empty] | SHASEガイドライン
1. Use specified units. |  |  |  | Program Version Release Date: |  |  |  | 2022-02-02 |  | Modeler Organization for Tables and Charts (short): |  |  |  | メーカ値
|  |  |  | Program Name for Tables and Charts (short): |  |  |  | QAS
2. Data entry is restricted to the following ranges: |  |  |  | Results Submission Date: |  |  |  | 2022-02-02 |  | Model / Organization Indentifier for Charts (short): |  |  |  | QAS/メーカ値
| C50..C52: | Software Name, Version, and Date of Results
| C61..I63: | Coil Loads, Fan Coil Air Handler, Cases AE101 - AE104
| M61..R75 | Detailed Outputs, Fan Coil Air Handler, Cases AE101-AE104
| C89..I95: | Coil Loads, Single Zone Air Handler, Cases AE201 - AE245
| M89..T123 | Detailed Outputs, Single Zone Air Handler, Cases AE201-AE245
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Standard 140, Section 6.5
[11 empty] | ツールの名称 | Quasi-analytic Solution
| Software: | Quasi-analytic Solution | [8 empty] | ツールのバージョン | V1
| Version: | V1 | [8 empty] | 試行者 | nino
| Date: | 2022-02-02 | [8 empty] | 実施日 | 2022-02-02
Last Hour of Simulation - Summary Outputs - 冷却水サブシステム
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.7815 | 5.0977 | 12 | 7 | 1512 | 37.08 | 2500.0002 | 31.94 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 31.94 | 16.1724 | 31.95 | 2500.0002 | 244.7305 | 1 | 1.2872 | 1.0775 | 527.4423 | 5.13 | 894.7683 | 409.7685 | 42.4425 | -5.14 | -896.5124 | -896.5124 | 0 | 0.01 | 1.7442 | 2.5024e-13
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | 31.0816 | 4.7383 | 12 | 7 | 1512 | 34.13 | 2500.0002 | 29.07 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 29.07 | 16.1724 | 29.08 | 2500.0002 | 244.7305 | 1 | 1.3576 | 1.1288 | 527.4423 | 5.05 | 880.8148 | 388.5199 | 35.1474 | -5.06 | -882.5589 | -882.5589 | 0 | 0.01 | 1.7442 | -9.0816e-14
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 29.7279 | 4.4595 | 12 | 7 | 1512 | 31.3 | 2500.0002 | 26.3 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 26.3 | 16.1724 | 26.31 | 2500.0002 | 244.7305 | 1 | 1.4194 | 1.1731 | 527.4423 | 4.99 | 870.3496 | 371.5988 | 28.6915 | -5 | -872.0938 | -872.0938 | 0 | 0.01 | 1.7442 | 2.2871e-14
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | 27.9871 | 4.1107 | 12 | 7 | 1512 | 26.4 | 2500.0002 | 17.78 | 1421.2392 | 8.14 | 106980 | 1 | 1078.761 | 2500.0002 | 21.5 | 16.1724 | 21.51 | 2500.0002 | 244.7305 | 1 | 1.5077 | 1.2355 | 527.4423 | 4.89 | 852.9078 | 349.8393 | 24.3739 | -8.62 | -854.7274 | -854.6519 | -0.075413 | 0.01 | 1.7442 | -0.075413
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | 32.5001 | 5.0375 | 12 | 7 | 1512 | 36.62 | 2500.0002 | 24.57 | 1062.6252 | 8.14 | 106980 | 1 | 1437.375 | 2500.0002 | 31.5 | 16.1724 | 31.51 | 2500.0002 | 244.7305 | 1 | 1.2983 | 1.0857 | 527.4423 | 5.11 | 891.2799 | 406.2511 | 42.4135 | -12.05 | -893.3473 | -893.0241 | -0.32321 | 0.01 | 1.7442 | -0.32321
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | 22.3164 | 3.05 | 10.75 | 7 | 1512 | 31.46 | 2500.0002 | 27.73 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 27.73 | 16.1724 | 27.74 | 2500.0002 | 244.7305 | 1 | 1.4181 | 1.1202 | 395.5817 | 3.72 | 648.8378 | 278.9554 | 25.6993 | -3.73 | -650.582 | -650.582 | 0 | 0.01 | 1.7442 | -9.0816e-14
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | 13.7967 | 1.674 | 9.5 | 7 | 1512 | 25.43 | 2500.0002 | 23 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 23 | 16.1724 | 23.01 | 2500.0002 | 244.7305 | 1 | 1.5292 | 1.0857 | 263.7211 | 2.42 | 422.0934 | 172.4582 | 14.086 | -2.43 | -423.8376 | -423.8376 | 0 | 0.01 | 1.7442 | 1.7319e-14
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | 9.5061 | 1.08 | 8.75 | 7 | 1512 | 23.21 | 2500.0002 | 9.23 | 305.496 | 8.14 | 106980 | 1 | 2194.5042 | 2500.0002 | 21.5 | 16.1724 | 21.51 | 2500.0002 | 244.7305 | 1 | 1.5536 | 0.98368 | 184.6048 | 1.7 | 296.5119 | 118.8265 | 6.9194 | -13.98 | -297.9654 | -298.2561 | 0.29067 | 0.01 | 1.7442 | 0.29067
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | 15.6679 | 1.9538 | 9.5 | 7 | 1512 | 34.02 | 2500.0002 | 20.66 | 471.6174 | 8.14 | 106980 | 1 | 2028.3828 | 2500.0002 | 31.5 | 16.1724 | 31.51 | 2500.0002 | 244.7305 | 1 | 1.3466 | 0.9875 | 263.7211 | 2.51 | 437.7911 | 195.8488 | 21.7789 | -13.36 | -439.5917 | -439.5353 | -0.056369 | 0.01 | 1.7442 | -0.056369
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.7815 | 5.0977 | 12 | 7 | 1512 | 37.08 | 2500.0002 | 31.94 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 31.94 | 16.4214 | 31.95 | 2500.0002 | 245 | 1 | 1.2872 | 1.076 | 527.4423 | 5.13 | 894.7683 | 409.7685 | 42.4425 | -5.14 | -896.5124 | -896.5124 | 0 | 0.01 | 1.7442 | 2.5024e-13
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 31.0816 | 4.7383 | 12 | 7 | 1512 | 34.13 | 2500.0002 | 29.07 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 29.07 | 16.4214 | 29.08 | 2500.0002 | 245 | 1 | 1.3576 | 1.1271 | 527.4423 | 5.05 | 880.8148 | 388.5199 | 35.1474 | -5.06 | -882.5589 | -882.5589 | 0 | 0.01 | 1.7442 | -9.0816e-14
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 29.7279 | 4.4595 | 12 | 7 | 1512 | 31.3 | 2499.9504 | 26.3 | 2499.9504 | 8.14 | 106980 | 1 | 0 | 2499.9504 | 26.3 | 16.4209 | 26.31 | 2499.9504 | 244.9957 | 1 | 1.4194 | 1.1714 | 527.4423 | 4.99 | 870.3323 | 371.5988 | 28.7088 | -5 | -872.0764 | -872.0764 | 0 | 0.01 | 1.7442 | 8.8818e-15
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 28.1341 | 4.1397 | 12 | 7 | 1512 | 27 | 2453.6622 | 22 | 2453.6622 | 3.0933 | 77488.41 | 0.724 | 0 | 2453.6622 | 22 | 15.9049 | 22.01 | 2453.6622 | 241.0038 | 0.991 | 1.4998 | 1.2728 | 527.4423 | 4.99 | 854.2175 | 351.6763 | 24.9011 | -5 | -855.9294 | -855.9294 | 0 | 0.01 | 1.7119 | -1.3101e-14
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.8205 | 5.1061 | 12 | 7 | 1512 | 37.13 | 2500.0002 | 32 | 2500.0002 | 1.1299 | 55391.22 | 0.518 | 0 | 2500.0002 | 32 | 16.4214 | 32.01 | 2500.0002 | 245 | 1 | 1.2856 | 1.1182 | 527.4423 | 5.12 | 893.0241 | 410.2557 | 44.6739 | -5.13 | -894.7683 | -894.7683 | 0 | 0.01 | 1.7442 | 1.3656e-13
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 22.2117 | 3.0315 | 10.75 | 7 | 1512 | 32.41 | 1871.9598 | 27.41 | 1871.9598 | 8.14 | 106979.85 | 1 | 0 | 1871.9598 | 27.41 | 10.1498 | 27.43 | 1871.9598 | 190.8378 | 0.87 | 1.4248 | 1.1793 | 395.5817 | 4.98 | 650.3977 | 277.6458 | 22.8298 | -5 | -653.0098 | -653.0098 | 0 | 0.02 | 2.612 | -1.1546e-14
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 13.7051 | 1.6606 | 9.5 | 7 | 1512 | 27.33 | 1251 | 22.42 | 1251 | 8.14 | 106980 | 1 | 0 | 1251 | 22.42 | 5.4534 | 22.43 | 1251 | 137.2862 | 0.703 | 1.5394 | 1.2401 | 263.7211 | 4.9 | 427.6678 | 171.314 | 7.3673 | -4.91 | -428.5406 | -428.5406 | 0 | 0.01 | 0.87279 | -5.7732e-15
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 9.508 | 1.0802 | 8.75 | 7 | 1512 | 24.95 | 1251 | 16.71 | 523.5012 | 0.52096 | 42792 | 0.4 | 727.4988 | 1251 | 21.5 | 5.4534 | 21.51 | 1251 | 137.2862 | 0.703 | 1.5533 | 1.338 | 184.6048 | 3.44 | 300.2403 | 118.8497 | 3.2142 | -8.24 | -300.9526 | -301.113 | 0.16047 | 0.01 | 0.87279 | 0.16047
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 15.6732 | 1.9546 | 9.5 | 7 | 1512 | 36.5 | 1275.474 | 26.83 | 659.6436 | 0.52096 | 42792 | 0.4 | 615.8304 | 1275.474 | 31.5 | 5.6113 | 31.51 | 1275.474 | 139.3969 | 0.71 | 1.3461 | 1.2106 | 263.7211 | 4.99 | 444.0433 | 195.9149 | 15.5928 | -9.67 | -445.0297 | -444.9332 | -0.096531 | 0.01 | 0.88987 | -0.096531
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | 13.7067 | 1.6609 | 9.5 | 7 | 1512 | 27.33 | 1251 | 22.43 | 1251 | 8.1343 | 106954.86 | 1 | 0 | 1251 | 22.43 | 5.4534 | 22.43 | 1251 | 137.2862 | 0.703 | 1.5392 | 1.24 | 263.7211 | 4.9 | 427.6678 | 171.334 | 7.3873 | -4.9 | -427.6678 | -427.6678 | 0 | 0 | 0 | 0
[11 empty] | 機器特性からの推定値 | 機器特性からの推定値 | 設定値 | 設定値 | 設定値 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 理論値
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37 | 527.4423 | 32.4 |  | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.6 | 395.5817 | 22.1 |  | 2.9
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.4 | 263.7211 | 13.8 |  | 1.8
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.9 | 395.5817 | 22.6 |  | 2.9
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37 | 453.4887 | 28.6 |  | 5.1
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37 | 527.4423 | 31.3 |  | 5.1

## BEST_二宮new
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | BEST2108 dev | [5 empty] | NIKKEN SEKKEI LTD nino
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2021-10-12 |  | Modeler Organization for Tables and Charts (short): |  |  |  | nino
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | BEST2108dev
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2021-10-12 |  | Model / Organization Indentifier for Charts (short): |  |  |  | BEST2108dev/nino | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | BEST2108
| Software: | BEST2108 | [8 empty] | ツールのバージョン | dev
| Version: | dev | [8 empty] | 試行者 | ninomiya
| Date: | 2022-01-26 | [8 empty] | 実施日 | 2022-01-26
定格冷水流量：1512L/min
| Last Hour of Simulation - Summary Outputs - 冷却水サブシステム | [6 empty] | 定格冷却水流量：2500L/min
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.4 | 5.1 | 12 | 7 | 1512 | 37.2 | 2500.0002 | 32 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 32 | 16.1724 | 32.08 | 2500.0002 | 244.7305 | 1 | 1.3023 | 1.0881 | 527.4423 | 5.12 | 893.0241 | 405 | 39.4182 | -5.2 | -906.9776 | -906.9776 | 0 | 0.08 | 13.9535 | 4.7962e-14 | -13.9535
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | 31.3628 | 5.1 | 12 | 7 | 1512 | 34.27 | 2500.0002 | 29.13 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 29.13 | 16.1724 | 29.22 | 2500.0002 | 244.7305 | 1 | 1.3454 | 1.118 | 527.4423 | 5.05 | 880.8148 | 392.0347 | 38.6622 | -5.14 | -896.5124 | -896.5124 | 0 | 0.09 | 15.6977 | 0 | -15.6977
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 30.3673 | 5.1 | 12 | 7 | 1512 | 31.46 | 2500.0002 | 26.38 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 26.38 | 16.1724 | 26.46 | 2500.0002 | 244.7305 | 1 | 1.3895 | 1.1483 | 527.4423 | 5 | 872.0938 | 379.5916 | 34.9401 | -5.08 | -886.0473 | -886.0473 | 0 | 0.08 | 13.9535 | -1.4211e-14 | -13.9535
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | 28.7027 | 5.1 | 12 | 7 | 1512 | 26.47 | 2500.0002 | 17.95 | 1457.8806 | 8.14 | 106980 | 1 | 1042.1196 | 2500.0002 | 21.5 | 16.1724 | 21.58 | 2500.0002 | 244.7305 | 1 | 1.4701 | 1.2028 | 527.4423 | 4.89 | 852.9078 | 358.7833 | 33.3178 | -8.52 | -866.5921 | -866.8613 | 0.26918 | 0.08 | 13.9535 | 0.26918 | -13.6843
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | 32.2508 | 5.1 | 12 | 7 | 1512 | 36.69 | 2500.0002 | 24.67 | 1080.4368 | 8.14 | 106980 | 1 | 1419.5634 | 2500.0002 | 31.5 | 16.1724 | 31.58 | 2500.0002 | 244.7305 | 1 | 1.3084 | 1.0923 | 527.4423 | 5.11 | 891.2799 | 403.1345 | 39.297 | -12.02 | -906.0601 | -905.2334 | -0.8267 | 0.08 | 13.9535 | -0.8267 | -14.7802
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | 22.4359 | 4.1445 | 10.75 | 7 | 1512 | 31.61 | 2500.0002 | 27.81 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 27.81 | 16.1724 | 27.89 | 2500.0002 | 244.7305 | 1 | 1.4105 | 1.1062 | 395.5817 | 3.72 | 648.8378 | 280.449 | 27.1929 | -3.8 | -662.7913 | -662.7913 | 0 | 0.08 | 13.9535 | 9.9476e-14 | -13.9535
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | 14.0131 | 3.5687 | 9.5 | 7 | 1512 | 25.61 | 2500.0002 | 23.1 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 23.1 | 16.1724 | 23.19 | 2500.0002 | 244.7305 | 1 | 1.5056 | 1.0517 | 263.7211 | 2.42 | 422.0934 | 175.1634 | 16.7912 | -2.51 | -437.7911 | -437.7911 | 0 | 0.09 | 15.6977 | 0 | -15.6977
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | 9.8193 | 3.4073 | 8.75 | 7 | 1512 | 23.28 | 2500.0002 | 9.43 | 321.063 | 8.14 | 106980 | 1 | 2178.9372 | 2500.0002 | 21.5 | 16.1724 | 21.58 | 2500.0002 | 244.7305 | 1 | 1.504 | 0.93286 | 184.6048 | 1.7 | 296.5119 | 122.7409 | 10.8338 | -13.85 | -310.2367 | -310.4654 | 0.22868 | 0.08 | 13.9535 | 0.22868 | -13.7248
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | 15.3875 | 3.5687 | 9.5 | 7 | 1512 | 34.09 | 2500.0002 | 20.76 | 486.1926 | 8.14 | 106980 | 1 | 2013.8076 | 2500.0002 | 31.5 | 16.1724 | 31.58 | 2500.0002 | 244.7305 | 1 | 1.3711 | 0.98428 | 263.7211 | 2.51 | 437.7911 | 192.344 | 18.2741 | -13.33 | -452.1595 | -451.7446 | -0.4149 | 0.08 | 13.9535 | -0.4149 | -14.3684
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.4 | 5.1 | 12 | 7 | 1512 | 37.2 | 2500.0002 | 32 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 32 | 16.4214 | 32.08 | 2500.0002 | 245 | 1 | 1.3023 | 1.0866 | 527.4423 | 5.12 | 893.0241 | 405 | 39.4182 | -5.2 | -906.9776 | -906.9776 | 0 | 0.08 | 13.9535 | 4.7962e-14 | -13.9535
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 31.3628 | 5.1 | 12 | 7 | 1512 | 34.27 | 2500.0002 | 29.13 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 29.13 | 16.4214 | 29.22 | 2500.0002 | 245 | 1 | 1.3454 | 1.1164 | 527.4423 | 5.05 | 880.8148 | 392.0355 | 38.6631 | -5.14 | -896.5124 | -896.5124 | 0 | 0.09 | 15.6977 | 0 | -15.6977
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 30.3674 | 5.1 | 12 | 7 | 1512 | 31.46 | 2500.0002 | 26.38 | 2500.0002 | 8.14 | 106980 | 1 | 0 | 2500.0002 | 26.38 | 16.4214 | 26.46 | 2500.0002 | 245 | 1 | 1.3895 | 1.1466 | 527.4423 | 5 | 872.0938 | 379.5924 | 34.9409 | -5.08 | -886.0473 | -886.0473 | 0 | 0.08 | 13.9535 | -1.4211e-14 | -13.9535
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 28.8712 | 5.1 | 12 | 7 | 1512 | 27 | 2488.7766 | 22 | 2488.7766 | 3.2294 | 78608.37 | 0.735 | 0 | 2488.7766 | 22 | 16.296 | 22.08 | 2488.7766 | 244.0321 | 0.997 | 1.4615 | 1.2333 | 527.4423 | 4.92 | 854.2877 | 360.89 | 34.0445 | -5 | -868.1786 | -868.1786 | 0 | 0.08 | 13.8909 | -2.1316e-13 | -13.8909
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.4 | 5.1 | 12 | 7 | 1512 | 37.2 | 2500.0002 | 32 | 2500.0002 | 1.1712 | 56058.63 | 0.524 | 0 | 2500.0002 | 32 | 16.4214 | 32.08 | 2500.0002 | 245 | 1 | 1.3023 | 1.1306 | 527.4423 | 5.12 | 893.0241 | 405 | 39.4182 | -5.2 | -906.9776 | -906.9776 | 0 | 0.08 | 13.9535 | 4.7962e-14 | -13.9535
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 22.6332 | 4.1445 | 10.75 | 7 | 1512 | 32.47 | 1894.104 | 27.47 | 1894.104 | 8.14 | 106979.79 | 1 | 0 | 1894.104 | 27.47 | 10.3444 | 27.54 | 1894.104 | 192.7475 | 0.875 | 1.3982 | 1.1491 | 395.5817 | 4.93 | 651.4842 | 282.9145 | 27.012 | -5 | -660.7345 | -660.7345 | 0 | 0.07 | 9.2503 | -7.4607e-14 | -9.2503
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 14.4538 | 3.5687 | 9.5 | 7 | 1512 | 27.4 | 1251 | 22.45 | 1251 | 8.14 | 106980 | 1 | 0 | 1251 | 22.45 | 5.4534 | 22.5 | 1251 | 137.2862 | 0.703 | 1.4597 | 1.1607 | 263.7211 | 4.9 | 427.6678 | 180.6721 | 16.7255 | -4.95 | -432.0318 | -432.0318 | 0 | 0.05 | 4.364 | -6.4837e-14 | -4.364
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 10.1948 | 3.4073 | 8.75 | 7 | 1512 | 24.99 | 1251 | 16.85 | 536.13 | 0.52096 | 42792 | 0.4 | 714.87 | 1251 | 21.5 | 5.4534 | 21.55 | 1251 | 137.2862 | 0.703 | 1.4486 | 1.2076 | 184.6048 | 3.44 | 300.2403 | 127.4352 | 11.7998 | -8.14 | -304.4722 | -304.6042 | 0.13199 | 0.05 | 4.364 | 0.13199 | -4.232
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 15.9479 | 3.5687 | 9.5 | 7 | 1512 | 36.5 | 1286.7474 | 26.93 | 672.1794 | 0.52096 | 42792 | 0.4 | 614.568 | 1286.7474 | 31.5 | 5.6848 | 31.55 | 1286.7474 | 140.3691 | 0.714 | 1.3229 | 1.1677 | 263.7211 | 4.95 | 444.3771 | 199.349 | 18.693 | -9.57 | -448.7974 | -448.8657 | 0.068382 | 0.05 | 4.4887 | 0.068382 | -4.4203
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | 14.4539 | 3.5687 | 9.5 | 7 | 1512 | 27.4 | 1251 | 22.45 | 1251 | 8.1162 | 106875.69 | 0.999 | 0 | 1251 | 22.45 | 5.4534 | 22.5 | 1251 | 137.2862 | 0.703 | 1.4597 | 1.1611 | 263.7211 | 4.9 | 427.6678 | 180.6742 | 16.7276 | -4.95 | -432.0318 | -432.0318 | 0 | 0.05 | 4.364 | -6.4837e-14 | -4.364
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37.12 | 527.4423 | 32.4 | 405 | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.71 | 395.5817 | 22.2071 | 277.589 | 4.1445
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.41 | 263.7211 | 13.8485 | 173.1058 | 3.5687
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.97 | 395.5817 | 22.4691 | 280.8632 | 4.1445
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37.13 | 453.4887 | 27.8871 | 348.5882 | 4.5194
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37.08 | 527.4423 | 31.6887 | 396.1088 | 5.1

## LCEM_矢島
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | LCEMツール Ver310 | [5 empty] | SHINRYO CORPORATION
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2022-01-31 |  | Modeler Organization for Tables and Charts (short): |  |  |  | Yajima
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | LCEM
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2022-01-31 |  | Model / Organization Indentifier for Charts (short): |  |  |  | LCEM/Yajima | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | LCEMツール
| Software: | LCEMツール | [8 empty] | ツールのバージョン | Ver310
| Version: | Ver310 | [8 empty] | 試行者 | 矢島和樹
| Date: | 2022-01-31 | [8 empty] | 実施日 | 2022-01-31
定格冷水流量：1512L/min
| Last Hour of Simulation - Summary Outputs - 冷却水サブシステム | [6 empty] | 定格冷却水流量：2500L/min
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3824 | 5.0997 | 12 | 7 | 1512 | 37 | 2500 | 32.0008 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 32.0008 | 16.6548 | 32.0192 | 2500 | 245.3962 | 1 | 1.303 | 1.0856 | 527.4423 | 4.9808 | 868.7383 | 404.78 | 63.4841 | -4.9992 | -871.9532 | -871.9532 | 0 | 0.018432 | 3.215 | 4.8406e-14
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | 30.9137 | 5.0997 | 12 | 7 | 1512 | 34 | 2500 | 29.158 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 29.158 | 16.6548 | 29.1765 | 2500 | 245.3962 | 1 | 1.3649 | 1.1282 | 527.4423 | 4.8235 | 841.3128 | 386.4206 | 72.5501 | -4.842 | -844.5278 | -844.5278 | 0 | 0.018432 | 3.215 | -6.5281e-14
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 29.6941 | 5.0997 | 12 | 7 | 1512 | 31.2 | 2500 | 26.4141 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 26.4141 | 16.6548 | 26.4326 | 2500 | 245.3962 | 1 | 1.421 | 1.1662 | 527.4423 | 4.7674 | 831.5274 | 371.1759 | 67.0909 | -4.7859 | -834.7423 | -834.7423 | 0 | 0.018432 | 3.215 | -6.5281e-14
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | 27.9962 | 5.0997 | 12 | 7 | 1512 | 26.2 | 2500 | 19.1321 | 1662.4327 | 8.1522 | 106980 | 1 | 837.5655 | 2500 | 21.5 | 16.6548 | 21.5184 | 2500 | 245.3962 | 1 | 1.5072 | 1.2237 | 527.4423 | 4.6816 | 816.5532 | 349.9526 | 60.8418 | -7.0679 | -819.7632 | -819.7681 | 0.0048991 | 0.018432 | 3.215 | 0.0048991
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | 32.1085 | 5.0997 | 12 | 7 | 1512 | 36.5 | 2500 | 26.5004 | 1250.0342 | 8.1522 | 106980 | 1 | 1249.964 | 2500 | 31.5 | 16.6548 | 31.5184 | 2500 | 245.3962 | 1 | 1.3142 | 1.0933 | 527.4423 | 4.9816 | 868.8788 | 401.3562 | 59.9197 | -9.9996 | -872.0871 | -872.0938 | 0.0066865 | 0.018432 | 3.215 | 0.0066865
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | 22.3625 | 4.9723 | 10.75 | 7 | 1512 | 31.5 | 2500 | 27.9077 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 27.9077 | 16.6548 | 27.9261 | 2500 | 245.3962 | 1 | 1.4152 | 1.098 | 395.5817 | 3.5739 | 623.3494 | 279.5314 | 51.7637 | -3.5923 | -626.5643 | -626.5643 | 0 | 0.018432 | 3.215 | 4.8406e-14
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | 13.9719 | 4.8448 | 9.5 | 7 | 1512 | 25.5 | 2500 | 23.1982 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 23.1982 | 16.6548 | 23.2166 | 2500 | 245.3962 | 1 | 1.51 | 1.034 | 263.7211 | 2.2834 | 398.265 | 174.6489 | 40.105 | -2.3018 | -401.48 | -401.48 | 0 | 0.018432 | 3.215 | -8.4377e-15
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | 9.7765 | 4.7684 | 8.75 | 7 | 1512 | 23.2 | 2500 | 15.0886 | 523.9642 | 8.1522 | 106980 | 1 | 1976.0376 | 2500 | 21.5 | 16.6548 | 21.5184 | 2500 | 245.3962 | 1 | 1.5106 | 0.91213 | 184.6048 | 1.6816 | 293.2969 | 122.2059 | 13.5138 | -8.1114 | -296.5172 | -296.5119 | -0.0052805 | 0.018432 | 3.215 | -0.0052805
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | 15.7341 | 4.8448 | 9.5 | 7 | 1512 | 34 | 2500 | 24.1065 | 631.7216 | 8.1522 | 106980 | 1 | 1868.2766 | 2500 | 31.5 | 16.6548 | 31.5184 | 2500 | 245.3962 | 1 | 1.3409 | 0.95184 | 263.7211 | 2.4816 | 432.8319 | 196.6765 | 27.5657 | -9.8935 | -436.0406 | -436.0469 | 0.0063108 | 0.018432 | 3.215 | 0.0063108
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3838 | 5.0997 | 12 | 7 | 1512 | 37 | 2498.1921 | 31.9994 | 2498.1921 | 8.1509 | 106974.6 | 0.99995 | 0 | 2498.1921 | 31.9994 | 16.5947 | 32.0179 | 2498.1921 | 244.6883 | 0.99861 | 1.303 | 1.0859 | 527.4423 | 4.9821 | 868.3516 | 404.7974 | 63.888 | -5.0006 | -871.5718 | -871.5718 | 0 | 0.018476 | 3.2202 | -7.1498e-14
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 31.023 | 5.0997 | 12 | 7 | 1512 | 34.3 | 2444.2833 | 29.249 | 2444.2833 | 8.1495 | 106968.3 | 0.99989 | 0 | 2444.2833 | 29.249 | 15.6267 | 29.2668 | 2444.2833 | 235.4971 | 0.97947 | 1.3601 | 1.1317 | 527.4423 | 5.0332 | 858.3151 | 387.7872 | 56.9144 | -5.051 | -861.3491 | -861.3491 | 0 | 0.017791 | 3.034 | -2.7978e-14
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 29.8244 | 5.0997 | 12 | 7 | 1512 | 31.5 | 2412.0149 | 26.4823 | 2412.0149 | 8.1466 | 106955.5 | 0.99977 | 0 | 2412.0149 | 26.4823 | 15.0664 | 26.4996 | 2412.0149 | 230.0914 | 0.96804 | 1.4148 | 1.1732 | 527.4423 | 5.0004 | 841.4613 | 372.8053 | 58.7863 | -5.0177 | -844.3875 | -844.3875 | 0 | 0.017389 | 2.9262 | -1.6875e-14
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 28.3404 | 5.0997 | 12 | 7 | 1512 | 27 | 2330.8252 | 21.9984 | 2330.8252 | 3.12 | 77671.6 | 0.72604 | 0 | 2330.8252 | 21.9984 | 13.7188 | 22.0144 | 2330.8252 | 216.808 | 0.93934 | 1.4889 | 1.2748 | 527.4423 | 4.9856 | 810.7305 | 354.2555 | 70.9673 | -5.0016 | -813.3388 | -813.3388 | 0 | 0.01604 | 2.6083 | -1.1546e-14
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.4024 | 5.0997 | 12 | 7 | 1512 | 37 | 2479.8717 | 31.9942 | 2479.8717 | 0.8093 | 49535.3 | 0.46303 | 0 | 2479.8717 | 31.9942 | 16.2612 | 32.0121 | 2479.8717 | 241.5423 | 0.9921 | 1.3022 | 1.134 | 527.4423 | 4.9879 | 862.9815 | 405.0301 | 69.4909 | -5.0058 | -866.0702 | -866.0702 | 0 | 0.017852 | 3.0887 | -8.8818e-14
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 23.2889 | 4.9723 | 10.75 | 7 | 1512 | 33 | 1840.6173 | 27.9885 | 1840.6173 | 8.1483 | 106963 | 0.99984 | 0 | 1840.6173 | 27.9885 | 7.3088 | 27.9996 | 1840.6173 | 146.268 | 0.76926 | 1.3589 | 1.1417 | 395.5817 | 5.0004 | 642.1246 | 291.1116 | 44.5687 | -5.0115 | -643.547 | -643.547 | 0 | 0.011077 | 1.4224 | -9.0594e-14
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 15.5699 | 4.8448 | 9.5 | 7 | 1512 | 28.5 | 1250 | 23.5884 | 1250 | 8.1353 | 106906.3 | 0.99931 | 0 | 1250 | 23.5884 | 2.8267 | 23.5947 | 1250 | 83.3 | 0.57653 | 1.355 | 1.1105 | 263.7211 | 4.9053 | 427.7871 | 194.6237 | 30.5578 | -4.9116 | -428.3392 | -428.3392 | 0 | 0.006331 | 0.55213 | 8.9373e-14
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 10.8457 | 4.7684 | 8.75 | 7 | 1512 | 24.9 | 1250 | 18.647 | 679.6655 | 0.52174 | 42792 | 0.4 | 570.3328 | 1250 | 21.5 | 2.8267 | 21.5063 | 1250 | 83.3 | 0.57653 | 1.3617 | 1.1715 | 184.6048 | 3.3937 | 295.9662 | 135.5713 | 24.2099 | -6.253 | -296.5077 | -296.5119 | 0.0041528 | 0.0062569 | 0.54566 | 0.0041528
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 17.3589 | 4.8448 | 9.5 | 7 | 1512 | 36.5 | 1290.8566 | 27.7256 | 735.5695 | 0.52174 | 42792 | 0.4 | 555.2854 | 1290.8566 | 31.5 | 3.0446 | 31.5065 | 1290.8566 | 86.8811 | 0.58918 | 1.2154 | 1.0998 | 263.7211 | 4.9935 | 449.7115 | 216.9861 | 30.9957 | -8.7744 | -450.2937 | -450.2992 | 0.005531 | 0.0065259 | 0.58772 | 0.005531
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | 15.5699 | 4.8448 | 9.5 | 7 | 1512 | 28.5 | 1250 | 23.5884 | 1250 | 8.1353 | 106906.3 | 0.99931 | 0 | 1250 | 23.5884 | 2.8267 | 23.5947 | 1250 | 83.3 | 0.57653 | 1.355 | 1.1105 | 263.7211 | 4.9053 | 427.7871 | 194.6237 | 30.5578 | -4.9116 | -428.3392 | -428.3392 | 0 | 0.006331 | 0.55213 | 8.9373e-14
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37.12 | 527.4423 | 32.4 | 405 | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.71 | 395.5817 | 22.2071 | 277.589 | 4.1445
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.41 | 263.7211 | 13.8485 | 173.1058 | 3.5687
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.97 | 395.5817 | 22.4691 | 280.8632 | 4.1445
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37.13 | 453.4887 | 27.8871 | 348.5882 | 4.5194
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37.08 | 527.4423 | 31.6887 | 396.1088 | 5.1

## ENe-ST_小野
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | ENe-ST | [5 empty] | 小野永吉
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 2022-02-09 |  | Modeler Organization for Tables and Charts (short): |  |  |  | 小野永吉
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | ENe-ST
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 2022-02-09 |  | Model / Organization Indentifier for Charts (short): |  |  |  | ENe-ST/小野永吉 | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | ENe-ST
| Software: | ENe-ST | [8 empty] | ツールのバージョン | -
| Version: | - | [8 empty] | 試行者 | 小野永吉
| Date: | 2022-02-09 | [8 empty] | 実施日 | 44601
Last Hour of Simulation - Summary Outputs - 冷却水サブシステム
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 32.3688 | 5.0625 | 12 | 7.0041 | 1512 | 36.716 | 2500 | 31.6295 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 31.6295 | 17.1008 | 31.718 | 2500 | 244.6318 | 0.99995 | 1.3025 | 1.0826 | 527.0063 | 4.998 | 871.7381 | 404.61 | 59.8782 | -5.0865 | -887.1769 | -887.1769 | 0 | 0.088516 | 15.4388 | 9.0594e-14
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | 30.7917 | 5.0625 | 12 | 7.0041 | 1512 | 33.545 | 2500 | 28.5548 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 28.5548 | 17.1008 | 28.6433 | 2500 | 244.6318 | 0.99995 | 1.3692 | 1.1283 | 527.0063 | 4.9017 | 854.9422 | 384.8967 | 56.9608 | -4.9902 | -870.381 | -870.381 | 0 | 0.088516 | 15.4388 | -1.3678e-13
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | 29.4763 | 5.0625 | 12 | 7.0041 | 1512 | 30.4744 | 2500 | 25.5645 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 25.5645 | 17.1008 | 25.653 | 2500 | 244.6318 | 0.99995 | 1.4303 | 1.1695 | 527.0063 | 4.8213 | 840.9326 | 368.4538 | 54.5274 | -4.9099 | -856.3715 | -856.3715 | 0 | 0.088516 | 15.4388 | -3.1974e-14
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | 28.0316 | 5.0625 | 12 | 7.0041 | 1512 | 26.3155 | 2500 | 14.1101 | 987.7083 | 8.1522 | 106980 | 1 | 1512.2917 | 2500 | 21.4938 | 17.1008 | 21.5823 | 2500 | 244.6318 | 0.99995 | 1.504 | 1.2183 | 527.0063 | 4.7331 | 825.5465 | 350.3951 | 51.8549 | -12.2054 | -841.073 | -840.9853 | -0.087683 | 0.088516 | 15.4388 | -0.087683
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | 32.294 | 5.0625 | 12 | 7.0041 | 1512 | 36.5751 | 2500 | 22.5544 | 906.2371 | 8.1522 | 106980 | 1 | 1593.7629 | 2500 | 31.4932 | 17.1008 | 31.5817 | 2500 | 244.6318 | 0.99995 | 1.3055 | 1.0847 | 527.0063 | 4.9934 | 870.9419 | 403.6755 | 59.7399 | -14.0207 | -886.472 | -886.3807 | -0.091243 | 0.088516 | 15.4388 | -0.091243
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | 22.2107 | 3.8 | 10.75 | 7 | 1512 | 31.0852 | 2500 | 27.3724 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 27.3724 | 17.1008 | 27.4609 | 2500 | 244.6318 | 0.99995 | 1.4248 | 1.1099 | 395.5817 | 3.6242 | 632.1287 | 277.634 | 41.087 | -3.7127 | -647.5676 | -647.5676 | 0 | 0.088516 | 15.4388 | 2.1316e-14
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | 13.7334 | 2.5333 | 9.5 | 7 | 1512 | 25.1099 | 2500 | 22.6708 | 2500 | 8.1522 | 106980 | 1 | 0 | 2500 | 22.6708 | 17.1008 | 22.7593 | 2500 | 244.6318 | 0.99995 | 1.5362 | 1.0677 | 263.7211 | 2.3506 | 409.9839 | 171.6679 | 25.4051 | -2.4391 | -425.4228 | -425.4228 | 0 | 0.088516 | 15.4388 | -2.3093e-14
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | 9.5428 | 1.7733 | 8.75 | 7 | 1512 | 23.2229 | 2500 | 7.2588 | 270.6879 | 8.1522 | 106980 | 1 | 2229.3121 | 2500 | 21.4932 | 17.1008 | 21.5818 | 2500 | 244.6318 | 0.99995 | 1.5476 | 0.9587 | 184.6048 | 1.6411 | 286.2372 | 119.2854 | 17.653 | -15.964 | -301.4843 | -301.676 | 0.19168 | 0.088516 | 15.4388 | 0.19168
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | 15.6117 | 2.5333 | 9.5 | 7 | 1512 | 34.0461 | 2500 | 19.4142 | 436.4167 | 8.1522 | 106980 | 1 | 2063.5833 | 2500 | 31.4923 | 17.1008 | 31.5808 | 2500 | 244.6318 | 0.99995 | 1.3514 | 0.97502 | 263.7211 | 2.4653 | 429.9875 | 195.1459 | 28.8796 | -14.6319 | -445.5084 | -445.4263 | -0.082161 | 0.088516 | 15.4388 | -0.082161
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 32.3693 | 5.0625 | 12 | 7.0041 | 1512 | 36.7195 | 2496.8163 | 31.6268 | 2496.8163 | 8.1522 | 106980 | 1 | 0 | 2496.8163 | 31.6267 | 17.0728 | 31.7151 | 2496.8163 | 244.4547 | 0.99952 | 1.3025 | 1.0828 | 527.0063 | 5.0044 | 871.7437 | 404.6165 | 59.8791 | -5.0928 | -887.1403 | -887.1577 | 0.017348 | 0.088486 | 15.414 | 0.017348
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | 30.8 | 5.0625 | 12 | 7.0041 | 1512 | 33.5951 | 2451.4726 | 28.5101 | 2451.4726 | 8.1522 | 106980 | 1 | 0 | 2451.4726 | 28.5101 | 16.2798 | 28.5959 | 2451.4726 | 236.712 | 0.98341 | 1.3688 | 1.1334 | 527.0063 | 4.9992 | 855.0305 | 385.0004 | 56.9761 | -5.085 | -869.7024 | -869.6992 | -0.0032177 | 0.085765 | 14.6687 | -0.0032177
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | 29.4942 | 5.0625 | 12 | 7.0041 | 1512 | 30.5625 | 2411.5328 | 25.4797 | 2411.5328 | 8.1522 | 106980 | 1 | 0 | 2411.5328 | 25.4797 | 15.6304 | 25.5632 | 2411.5328 | 230.0132 | 0.96925 | 1.4295 | 1.1793 | 527.0063 | 4.9993 | 841.123 | 368.6772 | 54.5605 | -5.0828 | -855.1596 | -855.1568 | -0.0027772 | 0.083412 | 14.0338 | -0.0027772
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | 28.264 | 5.0625 | 12 | 7.0041 | 1512 | 27.0891 | 2373.8933 | 22.0047 | 2373.8933 | 2.1549 | 68657.5295 | 0.64178 | 0 | 2373.8933 | 22.0083 | 15.0473 | 22.0896 | 2373.8933 | 223.7988 | 0.95593 | 1.4917 | 1.274 | 527.0063 | 4.9995 | 828.0218 | 353.3004 | 52.2849 | -5.0844 | -842.0786 | -841.4751 | -0.60353 | 0.081229 | 13.4533 | -0.60353
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | 32.5785 | 5.0625 | 12 | 7.0041 | 1512 | 37.1069 | 2500 | 32.0076 | 2500 | 1.0715 | 54393.5295 | 0.50845 | 0 | 2500 | 32.0076 | 17.1008 | 32.0962 | 2500 | 244.6318 | 0.99995 | 1.2941 | 1.1208 | 527.0063 | 5.0108 | 873.971 | 407.2307 | 60.266 | -5.0993 | -889.4098 | -889.4098 | 3.2336e-08 | 0.088516 | 15.4388 | 3.2336e-08
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | 22.3411 | 3.8 | 10.75 | 7 | 1512 | 31.822 | 1817.5682 | 26.7729 | 1817.5682 | 8.1522 | 106980 | 1 | 0 | 1817.5682 | 26.773 | 8.018 | 26.8261 | 1817.5682 | 143.3618 | 0.76278 | 1.4165 | 1.1865 | 395.5817 | 4.9959 | 633.5171 | 279.2636 | 41.3282 | -5.0491 | -640.2607 | -640.2463 | -0.014445 | 0.053066 | 6.7291 | -0.014445
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | 14.0256 | 2.5333 | 9.5 | 7 | 1512 | 26.7742 | 1250 | 22.005 | 1250 | 6.2764 | 98049.9326 | 0.91653 | 0 | 1250 | 22.005 | 3.8406 | 22.0374 | 1250 | 83.3017 | 0.57791 | 1.5042 | 1.2581 | 263.7211 | 4.7368 | 413.0958 | 175.3203 | 25.9456 | -4.7692 | -415.9219 | -415.9219 | 0 | 0.032406 | 2.8261 | 3.8192e-14
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | 9.8209 | 1.7733 | 8.75 | 7 | 1512 | 24.839 | 1250 | 12.9933 | 353.0027 | 0.52174 | 42792 | 0.4 | 896.9973 | 1250 | 21.4904 | 3.8406 | 21.5228 | 1250 | 83.3017 | 0.57791 | 1.5038 | 1.3243 | 184.6048 | 3.3161 | 289.1982 | 122.7607 | 18.1673 | -11.8457 | -291.7375 | -292.0243 | 0.28688 | 0.032406 | 2.8261 | 0.28688
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | 16.0614 | 2.5333 | 9.5 | 7 | 1512 | 36.5093 | 1250 | 24.7726 | 534.4175 | 0.52174 | 42792 | 0.4 | 715.5825 | 1250 | 31.4915 | 3.8406 | 31.5239 | 1250 | 83.3017 | 0.57791 | 1.3136 | 1.2017 | 263.7211 | 4.9854 | 434.7766 | 200.7669 | 29.7115 | -11.7367 | -437.6027 | -437.6027 | -5.6843e-12 | 0.032406 | 2.8261 | -5.7065e-12
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | 14.0256 | 2.5333 | 9.5 | 7 | 1512 | 26.7742 | 1250 | 22.005 | 1250 | 6.2764 | 98049.9326 | 0.91653 | 0 | 1250 | 22.005 | 3.8406 | 22.0374 | 1250 | 83.3017 | 0.57791 | 1.5042 | 1.2581 | 263.7211 | 4.7368 | 413.0958 | 175.3203 | 25.9456 | -4.7692 | -415.9219 | -415.9219 | 0 | 0.032406 | 2.8261 | 3.8192e-14
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37 | 527.4423 | 32.4 |  | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.6 | 395.5817 | 22.1 |  | 2.9
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.4 | 263.7211 | 13.8 |  | 1.8
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.9 | 395.5817 | 22.6 |  | 2.9
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37 | 453.4887 | 28.6 |  | 5.1
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37 | 527.4423 | 31.3 |  | 5.1

## Popolo_富樫
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Your Program | [5 empty] | 0
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 0 |  | Modeler Organization for Tables and Charts (short): |  |  |  | 0
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | Your Program
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 0 |  | Model / Organization Indentifier for Charts (short): |  |  |  | Your Program | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | Your Program
| Software: | Your Program | [8 empty] | ツールのバージョン
| Version: | 0 | [8 empty] | 試行者
| Date: | 0 | [8 empty] | 実施日
Last Hour of Simulation - Summary Outputs - 冷却水サブシステム
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37 | 527.4423 | 32.4 |  | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.6 | 395.5817 | 22.1 |  | 2.9
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.4 | 263.7211 | 13.8 |  | 1.8
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.9 | 395.5817 | 22.6 |  | 2.9
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37 | 453.4887 | 28.6 |  | 5.1
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37 | 527.4423 | 31.3 |  | 5.1

## ACSESCX_吉田
Output spreadsheet for 冷却水サブシステム Diagnostic Tests: CWS100 through CWSAR320
See "Adding Results" tab for more information. |  |  |  | Program Name and Version (with full build detail): | [5 empty] | Modeler Organization for Titles (long):
Paste new data in row 50 and below. |  |  |  | Your Program | [5 empty] | 0
Cells in blue are used in titles and labels |  |  |  | Program Version Release Date: |  |  |  | 0 |  | Modeler Organization for Tables and Charts (short): |  |  |  | 0
Editing them here flows thru to other tabs |  |  |  | Program Name for Tables and Charts (short): |  |  |  | Your Program
To print pdf file, see instructions on "Read Me" tab. |  |  |  | Results Submission Date: |  |  |  | 0 |  | Model / Organization Indentifier for Charts (short): |  |  |  | Your Program | defaults to short program name / short organization name
Content Instructions
1. Use specified units
2. Data entry is restricted to the following ranges:
| C50...C52: | Software Name, Version, and Date of Results
| L60…AF65: | 冷却水サブシステムテスト, CWS100 Series Cases
冷却塔単体テスト
冷却水ポンプ単体テスト
吸収式冷温水発生機単体テスト
3. Results are steady-state values for the last hour of the simulation.
4. Output terminology is defined in Section *.*
[11 empty] | ツールの名称 | Your Program
| Software: | Your Program | [8 empty] | ツールのバージョン
| Version: | 0 | [8 empty] | 試行者
| Date: | 0 | [8 empty] | 実施日
Last Hour of Simulation - Summary Outputs - 冷却水サブシステム
| Case No. | 境界条件・制御条件 | [8 empty] | 計算結果 | [19 empty] | 自動計算
|  | 外気 （OA） |  |  | 還り冷水 （wcR） |  | 吸収式冷温水発生機 （AR） |  | 冷却塔 （CT） | 三方弁 （V3W） | 吸収式冷温水発生機 （AR） | [6 empty] | 冷却塔 （CT） |  |  |  |  | 三方弁 （V3W） |  |  | 冷却水ポンプ （PCD）
|  | OA_乾球温度 | OA_湿球温度 | OA_相対湿度 | wcR_冷水定格流量比 | wcR_冷水入口温度 | AR_冷水出口設定温度 | AR_冷却水設定温度差 | 冷却塔ファン設定温度 | 三方弁設定温度 | AR_ガス消費量 | AR_消費電力 | AR_冷水入口温度 | AR_冷水出口温度 | AR_冷水流量 | AR_冷却水出口温度 | AR_冷却水流量 | CT_冷却水出口温度 | CT_冷却水流量 | CT_ファン消費電力 | CT_ファン風量 | CT_ファン回転数比 | V3W_入口B流量 | V3W_出口流量 | V3W_混合後温度 | PCD_消費電力 | PCD_出口水温 | PCD_出口流量 | PCD_揚程 | PCD_回転数比 | AR_COP | システム_COP | AR_冷水処理熱量 | AR_冷却水出入口温度差 | AR_冷却水放熱量 | AR_消費ガス熱量 | AR_排ガス放熱量 | CT_冷却水出入口温度差 | CT_冷却水冷却熱量 | V3W_冷却水放熱量 | CTとV3W_冷却水放熱量の差 | PCD_冷却水出入口温度差 | PCD_冷却水増加熱量 | 冷却水回路の熱収支
|  | Tdb_OA | Twb_OA | RH_OA | ratioWwcR_SET | TwcR_SET | Twc_AR_outSET | Tcd_AR_dSET | Tcd_CT_outSET | Tcd_V3W_SET |  |  | Twc_AR_in | Twc_AR_out | Wwc_AR_in | Tcd_AR_out | Wcd_AR_in | Tcd_CT_out | Wcd_CT_out |  |  |  | Wcd_V3W_inB | Wcd_V3W_out | Tcd_V3W_out |  | Tcd_PCD_out | Wcd_PCD_out
|  | ℃ | ℃ | ℃ | ％ | ℃ | ℃ | K | ℃ | ℃ | m3/h | kW | ℃ | ℃ | L/min | ℃ | L/min | ℃ | L/min | kW | m3/h | - | L/min | L/min | ℃ | kW | ℃ | L/min | kPa | - | - | - | kW | K | kW | kW | kW | K | kW | kW | kW | K | kW | kW
| S-CD100 | 36 | 27 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD101 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD102 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD103 | 11.7 | 7 | 50 | 100 | 12 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD104 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | ー | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD111 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD112 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD113 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | ー | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD114 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | ー | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD200 | 36 | 27 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD201 | 31.2 | 23 | 49.7 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD202 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD203 | 11.7 | 7 | 50 | 100 | 12 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD204 | 26.3 | 19 | 49.9 | 100 | 12 | 7 | 5 | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD211 | 31.2 | 23 | 49.7 | 100 | 10.75 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD212 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD213 | 11.7 | 7 | 50 | 100 | 8.75 | 7 | 5 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD214 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 5 | 32 | 31.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| S-CD215 | 26.3 | 19 | 49.9 | 100 | 9.5 | 7 | 6 | 22 | 21.5 | [20 empty] | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
冷却塔単体テスト
|  | 入力 | [6 empty] | 出力
| Case No. | 外気湿球温度 [℃] | 冷却水入口温度 [℃] | 風量 [%] | 水量 [%] | 冷却水出口温度 [℃] | ファン消費電力 [kW] | Case No. | 冷却水出口温度 [℃] | 消費電力 [kW]
| CT110 | 27 | 37 | 100 | 100 | 32 | 8.14 | CT110 | 31.97 | 8.1522
| CT120 | 23 | 33 | 100 | 75 | 28.1 | 8.14 | CT120 | 27.73 | 8.1522
| CT130 | 19 | 29 | 100 | 50 | 23.8 | 8.14 | CT130 | 23.1 | 8.1522
| CT140 | 15 | 25 | 100 | 25 | 19.2 | 8.14 | CT140 | 17.56 | 8.1522
| CT230 | 19 | 29 | 75 | 50 | 24.4 | 3.41 | CT230 | 23.97 | 3.4392
| CT240 | 15 | 25 | 50 | 25 | 20.5 | 1.01 | CT240 | 19.68 | 1.019
冷却水ポンプ単体テスト
吸収式冷温水機単体テスト(冷房)
| テスト条件 | [9 empty] | 出力
| Case No. | 負荷率 [%] | 処理能力 [kW] | 冷水入口温度[℃] | 冷水出口設定温度 [℃] | 冷水流量 [%] | 冷水流量[L/min] | 冷却水入口温度 [℃] | 冷却水流量 [%] | 冷却水 流量 [L/min] | 冷水出口温度[℃] | 冷却水出口温度[℃] | 処理能力[kW] | ガス消費量 [m3/h] | ガス消費量[kW] | 消費電力 [kW]
| AR110 | 100 | 527 | 12 | 7 | 100 | 1512 | 32 | 100 | 2500 | 7 | 37 | 527.4423 | 32.4 |  | 5.1
| AR120 | 75 | 395 | 10.75 | 7 | 100 | 1512 | 27 | 100 | 2500 | 7 | 30.6 | 395.5817 | 22.1 |  | 2.9
| AR130 | 50 | 264 | 9.5 | 7 | 100 | 1512 | 22 | 100 | 2500 | 7 | 24.4 | 263.7211 | 13.8 |  | 1.8
| AR210 | 75 | 395 | 12 | 7 | 75 | 1134 | 27 | 75 | 1875 | 7 | 31.9 | 395.5817 | 22.6 |  | 2.9
| AR310 | 86 | 453 | 10 | 5 | 86 | 1300 | 32 | 86 | 2150 | 5 | 37 | 453.4887 | 28.6 |  | 5.1
| AR320 | 100 | 527 | 14 | 9 | 100 | 1512 | 32 | 100 | 2500 | 9 | 37 | 527.4423 | 31.3 |  | 5.1