## はじめに
熱負荷シミュレーションツール
単室テスト・複数室テスト結果入力用ファイル
１．はじめに
本ファイルは熱負荷シミュレーションツールの単室テストおよび複数室テストの計算結果を入力するためのファイルです。
大部分はASHRAE Standard 140からの引用であり、Standardの付属ファイルから海外シミュレーションツールの計算結果を転載しています。
２．使用方法
「計算結果入力シート」の黄色セルにプログラム名称と計算結果を入力すると、「グラフ」に自動で結果が反映されます。
ASHRAE Standard 140で示されている海外ツールと、省エネシミュレーション評価法作成委員会にて試行した国内ツール（NewHASP、BEST、OFFICE）の結果と比較することができます。
2016-03-01
公益社団法人 空気調和・衛生工学会
空調システムのエネルギーシミュレーションツール評価法ガイドライン作成小委員会

## 計算結果入力シート
計算結果入力シート
このシートに計算結果を入力すると、「グラフ」シートのグラフに自動で表示されます。
※セル色の説明
→入力セル ⇒このセルに計算結果を入力してください。
→自動演算セル
グラフ表示用プログラム名称 ： |  |  | Your Program |  | →グラフの凡例としてこの名称が反映されます。
年間の暖房負荷、冷房負荷
ANNUAL HEATING LOADS
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 5.362 | 4.872 | 4.3871 | 5.4524 | 5.6857 | 4.994 | 4.3871
610 | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 5.383 | 4.97 | 4.4299 | 5.4888 | 5.8263 | 5.2341 | 4.4299
620 | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.728 | 5.073 | 4.5646 | 5.6118 | 5.8848 | 5.2042 | 4.5646
630 | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 |  | 5.624 | 4.8942 | 6.0366 | 6.5356 | 5.7664 | 4.8942
640 | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.309 | 3.043 | 2.6948 |  | 4.0695 | 2.5382 | 2.6948
650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 0 | 0.019809 | 0
900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 2.041 | 1.655 | 1.2286 | 1.7867 | 1.822 | 1.5153 | 1.2286
900-J1-1 | [8 empty] | 1.9854 | 3.0063 | 2.4214 | 2.6889 | 1.9854 | SHASE_G独自ケース
900-J1-2 | [8 empty] | 3.0803 | 4.1845 | 3.9625 | 3.9379 | 3.0803 | SHASE_G独自ケース
900-J2 | [8 empty] | 1.0566 | 1.5934 | 1.6905 | 1.8167 | 1.0566 | SHASE_G独自ケース
900-J3 | [8 empty] | 5.4785 | 5.3524 | 5.4406 | 5.7973 | 5.4785 | SHASE_G独自ケース
910 | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.22 | 2.097 | 1.5109 | 2.1821 | 2.6713 | 2.4018 | 1.5109
920 | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 4.3 | 3.776 | 3.2088 | 3.9527 | 4.782 | 3.6631 | 3.2088
930 | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 |  | 4.74 | 3.9205 | 4.9414 | 6.0858 | 4.7328 | 3.9205
940 | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.323 | 1.08 | 0.77258 |  | 1.5307 | 1.0648 | 0.77258
950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 0 | 0.02043 | 0
960 | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 2.816 | 3.373 | 2.4329 | 3.7485 | 3.5112 | 2.2663 | 2.4329
195 | 4.167 | [7 empty] | 4.6559 |  | 5.0239 | 5.0272 | 4.6559
200 | 5.252 | [7 empty] | 6.3154 |  | 7.834 | 7.0844 | 6.3154
210 | 6.456 | 6.559 |  |  |  |  | 6.967 | 6.554 | 6.606 |  | 8.5586 | 7.1394 | 6.606
215 | 5.547 | [7 empty] | 5.9495 | 7.6164 | 7.834 | 7.6898 | 5.9495
220 | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.437 | 7.297 | 7.115 | 8.5562 | 8.5586 | 7.7498 | 7.115
230 | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.964 | 10.84 | 10.9033 | 11.1587 | 12.0614 | 11.1882 | 10.9033
240 | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.234 | 6.076 | 5.8723 | 7.2242 | 7.9013 | 6.5127 | 5.8723
250 | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.738 | 5.764 | 5.195 | 6.8454 | 6.8145 | 6.2049 | 5.195
270 | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.489 | 5.047 | 4.4786 |  | 5.7677 | 0 | 4.4786
280 | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.841 | 5.279 |  |  | 5.7677 | 0 |  | SHASE_G対象外
290 | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.509 | 5.132 |  |  | 5.8868 | 0 |  | SHASE_G対象外
300 | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.786 | 5.124 |  |  | 6.3125 | 0 |  | SHASE_G対象外
310 | 5.221 | 5.327 |  | 5.85 | 6.165 |  |  | 5.61 |  |  | 6.3404 | 0 |  | SHASE_G対象外
320 | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.84 | 4.348 |  |  | 4.8056 | 0 |  | SHASE_G対象外
395 | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.839 | 4.855 | 4.9843 | 5.5824 | 5.3929 | 4.9687 | 4.9843
400 | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.326 | 7.166 | 7.0274 | 8.4334 | 8.4001 | 7.6663 | 7.0274
410 | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 9.085 | 8.936 | 8.914 | 9.7274 | 10.1404 | 9.4149 | 8.914
420 | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.863 | 7.697 | 7.6559 | 8.3803 | 9.4607 | 8.1512 | 7.6559
430 | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.51 | 6.5 | 6.028 | 7.0951 | 7.983 | 6.9227 | 6.028
440 | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.642 | 5.098 |  |  | 5.6857 | 0 |  | SHASE_G対象外
800 | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.861 | 5.94 | 6.4845 | 6.5324 | 7.6233 | 6.3488 | 6.4845
810 | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.962 | 2.567 |  |  | 1.822 | 0 |  | SHASE_G対象外
ANNUAL COOLING [MWH]
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh
600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.778 | 6.492 | 6.7453 | 7.2655 | 7.4541 | 7.9057 | 6.7453
610 | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 5.506 | 4.601 | 4.7484 | 4.9042 | 4.6982 | 4.2928 | 4.7484
620 | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 4.351 | 3.901 | 4.1709 | 4.5636 | 4.6445 | 5.1056 | 4.1709
630 | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 |  | 2.416 | 2.7837 | 2.6439 | 2.3089 | 3.0834 | 2.7837
640 | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.508 | 6.246 | 6.4599 |  | 7.3367 | 7.7112 | 6.4599
650 | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.456 | 5.119 | 5.3035 | 5.7031 | 5.6459 | 6.3344 | 5.3035
900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.599 | 2.485 | 2.5112 | 2.7841 | 2.7647 | 3.4899 | 2.5112
900-J1-1 | [8 empty] | 3.5402 | 4.3178 | 4.214 | 3.9287 | 3.5402 | SHASE_G独自ケース
900-J1-2 | [8 empty] | 1.6184 | 2.115 | 2.2312 | 2.0794 | 1.6184 | SHASE_G独自ケース
900-J2 | [8 empty] | 1.337 | 1.7128 | 1.8256 | 1.6662 | 1.337 | SHASE_G独自ケース
900-J3 | [8 empty] | 0.49076 | 1.3251 | 1.4425 | 1.0287 | 0.49076 | SHASE_G独自ケース
910 | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.767 | 1.326 | 1.2354 | 1.2058 | 0.67341 | 1.166 | 1.2354
920 | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.613 | 2.418 | 2.5522 | 2.6778 | 2.5272 | 3.3079 | 2.5522
930 | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 |  | 1.416 | 1.641 | 1.4385 | 1.1711 | 1.8763 | 1.641
940 | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.516 | 2.383 | 2.4368 |  | 2.091 | 3.3295 | 2.4368
950 | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.771 | 0.5606 | 0.53092 | 0.62267 | 0.48406 | 0.71387 | 0.53092
960 | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.786 | 0.4113 | 0.63915 | 0.19589 | 0.37033 | 0.6552 | 0.63915
195 | 0.414 | [7 empty] | 0.33399 |  | 0.52535 | 0.49803 | 0.33399
200 | 0.57 | [7 empty] | 0.43078 |  | 0.82213 | 0.73344 | 0.43078
210 | 0.162 | 0.613 |  |  |  |  | 0.641 | 0.6679 | 0.36507 |  | 0.61323 | 0.72191 | 0.36507
215 | 0.639 | [7 empty] | 0.64485 | 0.77043 | 0.82213 | 0.79184 | 0.64485
220 | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.683 | 0.7368 | 0.40633 | 0.51749 | 0.61323 | 0.77897 | 0.40633
230 | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 0.985 | 1.04 | 0.69551 | 0.73616 | 0.91367 | 1.0744 | 0.69551
240 | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.045 | 1.114 | 0.70418 | 0.82602 | 0.80677 | 1.1629 | 0.70418
250 | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 3.38 | 2.684 | 3.1867 | 2.3813 | 2.7746 | 2.758 | 3.1867
270 | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.714 | 8.764 | 8.1657 |  | 9.737 | 0 | 8.1657
280 | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 6.257 | 5.761 |  |  | 9.7404 | 0 |  | SHASE_G対象外
290 | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 7.431 | 6.699 |  |  | 6.8513 | 0 |  | SHASE_G対象外
300 | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.781 | 5.721 |  |  | 6.5252 | 0 |  | SHASE_G対象外
310 | 2.732 | 4.57 |  | 5.245 | 5.471 |  |  | 3.727 |  |  | 3.7648 | 0 |  | SHASE_G対象外
320 | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.663 | 5.956 |  |  | 6.6292 | 0 |  | SHASE_G対象外
395 | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.011 | 0.01029 | 0.0004087 | 0.0006336 | 0.0010522 | 0.021577 | 0.0004087
400 | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.044 | 0.04468 | 0.005787 | 0.0087888 | 0.011244 | 0.059988 | 0.005787
410 | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.065 | 0.06707 | 0.016158 | 0.016954 | 0.025222 | 0.082013 | 0.016158
420 | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.143 | 0.1575 | 0.067594 | 0.071534 | 0.056398 | 0.17827 | 0.067594
430 | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.875 | 0.6174 | 0.65185 | 0.47298 | 0.43784 | 0.64355 | 0.65185
440 | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 4.684 | 3.975 |  |  | 7.4541 | 0 |  | SHASE_G対象外
800 | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.325 | 0.2073 | 0.064574 | 0.10089 | 0.18422 | 0.2287 | 0.064574
810 | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.624 | 1.191 |  |  | 2.7647 | 0 |  | SHASE_G対象外
最大暖房負荷
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW
600 | 3.437 | 3.94 | 4.045 | 4.258 |  | 4.037 | 4.354 | 3.9306 | 3.7518 | 4.0512 | 4.3411 | 4.072 | 3.7518
610 | 3.437 | 3.941 | 4.034 | 4.258 |  | 4.037 | 4.354 | 3.9222 | 3.7413 | 4.032 | 4.3272 | 4.079 | 3.7413
620 | 3.591 | 3.941 | 4.046 | 4.277 |  | 4.277 | 4.379 | 3.9222 | 3.7411 | 4.0512 | 4.343 | 4.0895 | 3.7411
630 | 3.592 | 3.941 | 4.025 | 4.28 |  | 4.278 |  | 3.9222 | 3.7209 | 4.0224 | 4.3166 | 4.0918 | 3.7209
640 | 5.232 | 5.486 | 5.943 | 6.53 |  | 6.347 | 6.954 | 5.7222 | 6.3682 |  | 8.376 | 6.7569 | 6.3682
650 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
900 | 2.85 | 3.453 | 3.557 | 3.76 |  | 3.608 | 3.797 | 3.5167 | 3.1744 | 3.7104 | 3.947 | 3.65 | 3.1744
900-J1-1 | [8 empty] | 3.4047 | 3.8688 | 3.9432 | 3.9348 | 3.4047 | SHASE_G独自ケース
900-J1-2 | [8 empty] | 4.2401 | 4.6512 | 5.1082 | 4.8453 | 4.2401 | SHASE_G独自ケース
900-J2 | [8 empty] | 7.1306 | 10.1232 | 11.3803 | 9.1232 | 7.1306 | SHASE_G独自ケース
900-J3 | [8 empty] | 4.5872 | 4.7712 | 5.1158 | 5.0453 | 4.5872 | SHASE_G独自ケース
910 | 2.858 | 3.456 | 3.564 | 3.764 |  | 3.618 | 3.801 | 3.5361 | 3.1742 | 3.7056 | 4.2302 | 3.7023 | 3.1742
920 | 3.308 | 3.703 | 3.805 | 4.013 |  | 4.029 | 4.061 | 3.7083 | 3.4842 | 3.84 | 4.4131 | 3.8267 | 3.4842
930 | 3.355 | 3.732 | 3.832 | 4.042 |  | 4.064 |  | 3.7444 | 3.5074 | 3.8448 | 4.4371 | 3.8825 | 3.5074
940 | 3.98 | 5.028 | 5.665 | 6.116 |  | 6.117 | 6.428 | 5.1222 | 4.8682 |  | 8.1427 | 6.3988 | 4.8682
950 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
960 | 2.41 | 2.751 | 2.727 | 2.863 |  | 2.852 | 2.779 | 2.522 | 2.7006 | 2.2464 | 2.797 | 2.6349 | 2.7006
195 | 2.004 | [7 empty] | 2.1428 |  | 2.2906 | 2.286 | 2.1428
200 | 2.651 | [7 empty] | 2.9952 |  | 3.588 | 3.2616 | 2.9952
210 | 2.701 | 2.973 |  |  |  |  | 3.325 | 2.9806 | 3.0445 |  | 3.7003 | 3.2628 | 3.0445
215 | 2.787 | [7 empty] | 3.0338 | 3.4704 | 3.588 | 3.5383 | 3.0338
220 | 2.867 | 3.28 | 3.465 | 3.695 |  | 3.348 | 3.52 | 3.3361 | 3.2464 | 3.6192 | 3.7003 | 3.5407 | 3.2464
230 | 4.386 | 4.984 | 4.994 | 5.279 |  | 5.159 | 5.107 | 4.8917 | 5.0669 | 4.7712 | 5.2622 | 5.0697 | 5.0669
240 | 2.685 | 3.1 | 3.282 | 3.495 |  | 3.159 | 3.333 | 3.1528 | 3.0628 | 3.432 | 3.6734 | 3.3558 | 3.0628
250 | 2.866 | 3.279 | 3.465 | 3.695 |  | 3.341 | 3.525 | 3.3361 | 3.2463 | 3.6192 | 3.7003 | 3.5395 | 3.2463
270 | 2.863 | 3.277 |  | 3.661 |  |  | 3.738 | 3.3361 | 3.0253 |  | 3.5885 | 0 | 3.0253
280 | 2.864 | 3.278 |  | 3.685 |  |  | 3.759 | 3.3361 |  |  | 3.5885 | 0 |  | SHASE_G対象外
290 | 2.863 | 3.277 |  | 3.661 |  |  | 3.738 | 3.3278 |  |  | 3.5755 | 0 |  | SHASE_G対象外
300 | 3.014 | 3.276 |  | 3.681 |  |  | 3.77 | 3.3278 |  |  | 3.8525 | 0 |  | SHASE_G対象外
310 | 3.015 | 3.277 |  | 3.669 |  |  |  | 3.3278 |  |  | 3.5678 | 0 |  | SHASE_G対象外
320 | 2.861 | 3.275 |  | 3.651 |  |  | 3.735 | 3.3361 |  |  | 3.588 | 0 |  | SHASE_G対象外
395 | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.27 | 2.2211 | 2.2333 | 2.3856 | 2.3674 | 2.3 | 2.2333
400 | 2.867 | 3.28 | 3.476 | 3.695 |  | 3.342 | 3.52 | 3.3361 | 3.2464 | 3.6192 | 3.7003 | 3.5662 | 3.2464
410 | 3.625 | 4.124 | 4.233 | 4.487 |  | 4.227 | 4.314 | 4.1139 | 4.1567 | 4.1952 | 4.4717 | 4.3453 | 4.1567
420 | 3.443 | 3.944 | 4.05 | 4.287 |  | 4.044 | 4.126 | 3.9306 | 3.973 | 4.008 | 4.4429 | 4.1593 | 3.973
430 | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 4.137 | 3.9306 | 3.973 | 4.0032 | 4.4429 | 4.1581 | 3.973
440 | 3.439 | 3.942 |  | 4.277 |  |  | 4.376 | 3.9306 |  |  | 4.3411 | 0 |  | SHASE_G対象外
800 | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.939 | 3.7861 | 3.8183 | 3.8688 | 4.3877 | 4.0034 | 3.8183
810 | 2.979 | 3.566 |  | 3.915 |  |  | 3.963 | 3.6056 |  |  | 3.947 | 0 |  | SHASE_G対象外
最大冷房負荷
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW
600 | 6.194 | 5.965 | 6.656 | 6.827 |  | 6.286 | 6.812 | 6.4861 | 6.5686 | 6.4608 | 7.0992 | 7.0895 | 6.5686
610 | 5.669 | 5.824 | 6.064 | 6.371 |  | 6.17 | 6.146 | 5.675 | 6.1674 | 6.2688 | 6.6312 | 5.7639 | 6.1674
620 | 3.634 | 4.075 | 4.43 | 4.593 |  | 4.297 | 5.096 | 4.275 | 3.9234 | 4.224 | 4.4573 | 5.043 | 3.9234
630 | 3.072 | 3.704 | 3.588 | 4.116 |  | 3.665 |  | 3.6083 | 3.3784 | 3.5856 | 3.4166 | 4.1209 | 3.3784
640 | 6.161 | 5.892 | 6.576 | 6.776 |  | 6.25 | 6.771 | 6.4417 | 6.5043 |  | 7.0838 | 7.0604 | 6.5043
650 | 6.031 | 5.831 | 6.516 | 6.671 |  | 6.143 | 6.679 | 6.3778 | 6.3742 | 6.3648 | 6.9163 | 6.9499 | 6.3742
900 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.457 | 3.5667 | 3.2552 | 3.4128 | 3.8707 | 4.0907 | 3.2552
900-J1-1 | [8 empty] | 4.0622 | 4.3392 | 4.4597 | 3.9988 | 4.0622 | SHASE_G独自ケース
900-J1-2 | [8 empty] | 2.6921 | 3.3552 | 3.445 | 3.2569 | 2.6921 | SHASE_G独自ケース
900-J2 | [8 empty] | 2.8468 | 3.456 | 3.6197 | 3.4151 | 2.8468 | SHASE_G独自ケース
900-J3 | [8 empty] | 1.5426 | 2.9424 | 3.1723 | 2.693 | 1.5426 | SHASE_G独自ケース
910 | 1.896 | 2.5 | 2.336 | 3.277 |  | 2.786 | 3.147 | 2.7917 | 2.5779 | 2.664 | 2.459 | 2.107 | 2.5779
920 | 2.385 | 2.933 | 3.109 | 3.487 |  | 3.071 | 3.505 | 3.05 | 2.7822 | 3.2496 | 3.1848 | 3.7093 | 2.7822
930 | 1.873 | 2.546 | 2.388 | 3.08 |  | 2.486 |  | 2.4983 | 2.2789 | 2.6256 | 2.4528 | 2.9174 | 2.2789
940 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.457 | 3.5667 | 3.2551 |  | 3.4114 | 4.0907 | 3.2551
950 | 2.033 | 2.621 | 2.664 | 3.17 |  | 2.677 | 2.867 | 2.6861 | 2.3924 | 2.7792 | 3.0086 | 3.2209 | 2.3924
960 | 0.953 | 1.144 | 1.057 | 1.37 |  | 1.179 | 1.403 | 1.378 | 1.1419 | 0.8592 | 1.0411 | 0.99999 | 1.1419
195 | 0.651 | [7 empty] | 0.65384 |  | 0.83856 | 0.80348 | 0.65384
200 | 0.863 | [7 empty] | 0.8503 |  | 1.2998 | 1.1442 | 0.8503
210 | 0.476 | 1.017 |  |  |  |  | 1.142 | 1.0678 | 0.81173 |  | 1.139 | 1.1442 | 0.81173
215 | 1.007 | [7 empty] | 1.074 | 1.2288 | 1.2998 | 1.2477 | 1.074
220 | 0.56 | 1.166 | 0.937 | 1.34 |  | 1.215 | 1.213 | 1.1789 | 0.90998 | 1.0992 | 1.139 | 1.2465 | 0.90998
230 | 1.059 | 1.646 | 1.455 | 1.875 |  | 1.7 | 1.749 | 1.7078 | 1.4067 | 1.4784 | 1.6517 | 1.7581 | 1.4067
240 | 0.739 | 1.347 | 1.119 | 1.54 |  | 1.398 | 1.397 | 1.3614 | 1.0927 | 1.2864 | 1.2523 | 1.4535 | 1.0927
250 | 3.36 | 3.036 | 2.605 | 2.59 |  | 2.258 | 4.912 | 3.2278 | 3.0393 | 2.2608 | 2.4634 | 2.4267 | 3.0393
270 | 6.356 | 6.641 |  | 7.234 |  |  | 6.867 | 6.7639 | 6.6298 |  | 7.4486 | 0 | 6.6298
280 | 4.444 | 4.631 |  | 5.22 |  |  | 5.236 | 4.7861 |  |  | 7.4486 | 0 |  | SHASE_G対象外
290 | 6.269 | 6.555 |  | 6.976 |  |  | 6.621 | 6.2028 |  |  | 7.091 | 0 |  | SHASE_G対象外
300 | 3.404 | 4.093 |  | 4.657 |  |  | 4.929 | 4.2778 |  |  | 4.5754 | 0 |  | SHASE_G対象外
310 | 2.848 | 3.749 |  | 4.164 |  |  |  | 3.5889 |  |  | 3.444 | 0 |  | SHASE_G対象外
320 | 5.701 | 5.946 |  | 6.553 |  |  | 6.141 | 6.1778 |  |  | 6.8064 | 0 |  | SHASE_G対象外
395 | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.345 | 0.3625 | 0.07329 | 0.2112 | 0.2064 | 0.37209 | 0.07329
400 | 0 | 0.581 | 0.265 | 0.666 |  | 0.612 | 0.572 | 0.61333 | 0.25475 | 0.4656 | 0.45648 | 0.64999 | 0.25475
410 | 0.035 | 0.699 | 0.413 | 0.814 |  | 0.724 | 0.71 | 0.74306 | 0.3952 | 0.5712 | 0.60864 | 0.79185 | 0.3952
420 | 0.258 | 0.923 | 0.631 | 1.047 |  | 0.938 | 0.921 | 0.93778 | 0.6316 | 0.8064 | 0.75024 | 1.0105 | 0.6316
430 | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 2.578 | 1.7983 | 1.7304 | 1.512 | 1.5384 | 1.6791 | 1.7304
440 | 4.546 | 4.424 |  | 5.053 |  |  | 5.278 | 4.6861 |  |  | 7.0992 | 0 |  | SHASE_G対象外
800 | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 1.358 | 0.98278 | 0.52505 | 0.9168 | 1.237 | 1.1325 | 0.52505
810 | 1.852 | 2.357 |  | 2.991 |  |  | 2.862 | 2.3436 |  |  | 3.8707 | 0 |  | SHASE_G対象外
自然室温
FREE-FLOAT TEMPERATURE OUTPUT
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
600FF | 64.929 | 65.11 | 69.5 | 68.6 |  | 64.9 | 65.25 | 65.25 | 65.275 | 64.88 | 64.74 | 69.5 | 65.275
900FF | 41.812 | 43.44 | 42.7 | 44.8 |  | 43 | 43.17 | 42.46 | 43.1725 | 42.65 | 42.66 | 44.5 | 43.1725
650FF | 63.236 | 63.45 | 68.2 | 67 |  | 63.3 | 63.82 | 63.74 | 63.4835 | 63.42 | 62.58 | 66.6 | 63.4835
950FF | 35.54 | 36.23 | 35.9 | 38.5 |  | 36.1 | 37.58 | 35.67 | 36.6456 | 35.57 | 35.36 | 36.6 | 36.6456
960 | 48.943 | 48.88 | 49 | 51 |  | 50.2 | 48.92 | 55.34 | 51.4704 | 55.86 | 53.98 | 55.4 | 51.4704
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA |  | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
600FF | -15.565 | -17.05 | -18.8 | -18 |  | -17.8 | -18.47 | -17.81 | -17.5283 | -19.99 | -19.56 | -17.7 | -17.5283
900FF | -1.647 | -3.15 | -4.3 | -4.5 |  | -4 | -5.64 | -6.38 | -2.6597 | -4.35 | -4.21 | -2.8 | -2.6597
650FF | -22.564 | -22.96 | -21.6 | -23 |  | -22.9 | -22.91 | -22.83 | -23.0439 | -23.25 | -23.4 | -22.9 | -23.0439
950FF | -19.484 | -20.04 | -18.6 | -19.7 |  | -20.2 | -19.96 | -19.34 | -20.3396 | -19.03 | -20.07 | -19.8 | -20.3396
960 | 2.729 | 1.63 | 3.9 | 3.1 |  | 1.4 | -0.39 | -2.82 | 2.1322 | -2.41 | 1.74 | 4.3 | 2.1322
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
600FF | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.22 | 24.49 | 25.8015 | 25.3518 | 25.2127 | 26.7084 | 25.8015
900FF | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.45 | 24.47 | 25.9963 | 25.4076 | 25.2464 | 26.7685 | 25.9963
650FF | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 18.36 | 17.99 | 18.6305 | 19.3174 | 18.0921 | 18.6483 | 18.6305
950FF | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.64 | 14.53 | 14.4891 | 14.9374 | 13.8294 | 14.3331 | 14.4891
960 | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 26.43 | 28.96 | 28.7726 | 31.1696 | 30.3189 | 31.8204 | 28.7726
年間積算日射量（全天） | [14 empty] | 窓の日射透過係数 →自動演算
SOLAR RADIATION | [14 empty] | ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
ANNUAL INCIDENT TOTAL | [14 empty] | (ANNUAL UNSHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED INCIDENT SOLRAD)
CASE 600
[15 empty] | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program |  | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | FINLAND | BEL/UK | USA
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN |  |  | CASE#
SURFACE | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
= | = | = | = | = | = | = | = | = | = | = | = | = |  |  | 620WEST | 0.67403 | #DIV/0! | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.64771 | 0.65382 | 0.64806 | #DIV/0! | 0 | 0.66694 | 0.64806
NORTH | 427 |  | 434 | 456 | 407.3 | 457 | 453 | 367.4 | 432.1342 |  | 430.235 | 432.1452 | 432.1342 |  | 600SOUTH | 0.64973 | #DIV/0! | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.62262 | 0.64663 | 0.63455 | #DIV/0! | 0 | 0.64998 | 0.63455
EAST | 959 |  | 1155 | 1083 | 1217.3 | 1082 | 962 | 1101 | 1179.2605 |  | 1173.544 | 1007.7402 | 1179.2605
WEST | 1086 |  | 1079 | 1003 | 856.5 | 1002 | 1090 | 1012 | 1040.5181 |  | 1042.939 | 1200.5253 | 1040.5181
SOUTH | 1456 |  | 1566 | 1476 | 1467.7 | 1474 | 1468 | 1522 | 1544.9789 |  | 1546.351 | 1537.6279 | 1544.9789
HORZ. | 1797 |  | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1840.0607 |  | 1849.656 | 1831.8356 | 1840.0607
= | = | = | = | = | = | = | = | = | = | = | = | =
窓の庇による日射遮蔽係数 →自動演算
ANNUAL SHADING COEFFICIENT OF WINDOW SHADING DEVICES: OVERHANGS & FINS
(1-(ANNUAL SHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED TRANSMITTED SOLRAD))
[15 empty] | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
年間積算透過日射量（全天、庇なし） | [14 empty] | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | FINLAND | BEL/UK | USA
SOLAR RADIATION | [14 empty] | CASE#
UNSHADED ANNUAL TRANSMITTED
[15 empty] | 630/620 W | 0.18169 | #DIV/0! | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 1 | 0.33879 | 0.27706 | #DIV/0! | #DIV/0! | 0.3375 | 0.27706
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program |  | 610/600 S | 0.17019 | #DIV/0! | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.11488 | 0.20542 | 0.19642 | #DIV/0! | #DIV/0! | 0.34126 | 0.19642
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
620WEST | 732 |  | 735 | 689 | 562.96 | 642 | 706 | 661.67 | 674.319 |  |  | 800.6768 | 674.319
600SOUTH | 946 |  | 1051 | 962 | 954.3 | 926 | 914 | 984.17 | 980.3665 |  |  | 999.4199 | 980.3665
= | = | = | = | = | = | = | = | = | = | = | = | =
年間積算透過日射量（全天、庇あり）
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
630WEST | 599 |  | 481 | 554 | 441.3 | 431 |  | 437.5 | 487.4921 |  |  | 530.4459 | 487.4921
610SOUTH | 785 |  | 831 | 803 | 774.86 | 757 | 809 | 782 | 787.8056 |  |  | 658.3534 | 787.8056
= | = | = | = | = | = | = | = | = | = | = | = | =
曇天日3/5の南面日射量（Case 600）
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3 | 3.05 | 4.1392 |  | 3 | 2.0814 | 4.1392
8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.68 | 20.69 | 19.9066 |  | 21 | 19.6626 | 19.9066
9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 35.4789 |  | 39 | 38.3019 | 35.4789
10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.56 | 54.67 | 48.9837 |  | 55 | 54.5226 | 48.9837
11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 65.99 | 66.08 | 58.4496 |  | 66 | 66.476 | 58.4496
12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.74 | 71.92 | 63.7276 |  | 73 | 72.4876 | 63.7276
13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.3 | 72.42 | 63.4692 |  | 73 | 73.2434 | 63.4692
14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.38 | 66.53 | 57.1639 |  | 67 | 67.2434 | 57.1639
15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 54.8 | 55 | 46.1404 |  | 55 | 55.3599 | 46.1404
16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.84 | 38.94 | 31.7261 |  | 39 | 38.4879 | 31.7261
17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.46 | 20.52 | 15.6423 |  | 20 | 20.1858 | 15.6423
18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 0 | 3.05 | 2.6702 |  | 3 | 0 | 2.6702
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | = | = | = | =
曇天日3/5の西面日射量（Case 600）
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 3 | 2.99 | 4.1007 |  | 3 | 2.9767 | 4.1007
8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.15 | 20.17 | 19.5371 |  | 20 | 20.8835 | 19.5371
9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.9 | 37.92 | 34.5799 |  | 38 | 38.2903 | 34.5799
10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.15 | 53.17 | 47.8212 |  | 53 | 53.2087 | 47.8212
11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.4 | 64.39 | 56.9729 |  | 64 | 63.8598 | 56.9729
12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.95 | 69.89 | 61.3278 |  | 69 | 69.1039 | 61.3278
13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 71.16 | 70.75 | 61.4275 |  | 70 | 70.7667 | 61.4275
14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 66.02 | 65.69 | 56.2762 |  | 65 | 66.383 | 56.2762
15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.16 | 55.03 | 46.1267 |  | 55 | 55.7087 | 46.1267
16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.73 | 39.61 | 32.2501 |  | 39 | 39.0112 | 32.2501
17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.6 | 21.42 | 16.1236 |  | 21 | 19.6626 | 16.1236
18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 0 | 3.28 | 2.7155 |  | 3 | 0 | 2.7155
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | = | = | = | =
晴天日7/27の南面日射量（Case 600）
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.2 | 0.17 | 2.8637 |  | 0 | 0 | 2.8637
6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 25.7 | 27.01 | 35.6572 |  | 27 | 26.0578 | 35.6572
7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 62.1 | 63 | 90.2926 |  | 85 | 73.2317 | 90.2926
8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 107.47 | 71.22 | 136.1384 |  | 125 | 123.7196 | 136.1384
9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 232.33 | 187.72 | 256.058 |  | 240 | 257.5669 | 256.058
10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 349.16 | 314.17 | 377.0924 |  | 366 | 369.9726 | 377.0924
11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 430.22 | 404.44 | 449.9555 |  | 448 | 441.1463 | 449.9555
12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 459.85 | 443.61 | 468.97 |  | 467 | 461.1577 | 468.97
13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 462.28 | 452.5 | 458.4652 |  | 467 | 454.8438 | 458.4652
14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 404.57 | 400.56 | 395.7752 |  | 407 | 391.3561 | 395.7752
15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 319.26 | 316.94 | 298.2775 |  | 317 | 299.1013 | 298.2775
16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 193.61 | 188.89 | 170.2592 |  | 187 | 165.4517 | 170.2592
17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 132.3 | 86.03 | 80.3704 |  | 81 | 97.3129 | 80.3704
18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 76.6 | 69.78 | 52.387 |  | 62 | 61.7668 | 52.387
19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 18.05 | 17.61 | 15.1854 |  | 17 | 15.6742 | 15.1854
20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | = | = | = | =
晴天日7/27の西面日射量（Case 600）
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.2 | 0.17 | 2.8637 |  | 0 | 0 | 2.8637
6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 25.7 | 27.01 | 35.6572 |  | 27 | 26.0578 | 35.6572
7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 62.1 | 63 | 90.2926 |  | 85 | 73.2317 | 90.2926
8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 72 | 71.22 | 128.8229 |  | 125 | 97.9408 | 128.8229
9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 92.6 | 85.58 | 146.3844 |  | 145 | 116.4289 | 146.3844
10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 112.8 | 98.03 | 152.7179 |  | 153 | 129.0218 | 152.7179
11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 136.75 | 109.14 | 149.8255 |  | 150 | 134.4985 | 149.8255
12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 150.9 | 113.06 | 142.658 |  | 140 | 133.4404 | 142.658
13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 382.5 | 235.17 | 257.4 |  | 230 | 347.1008 | 257.4
14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 576.81 | 453.89 | 457.0081 |  | 433 | 554.3427 | 457.0081
15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 744.52 | 652.5 | 616.3624 |  | 606 | 735.5267 | 616.3624
16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 807.29 | 762.78 | 668.525 |  | 691 | 830.5954 | 668.525
17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 541.68 | 568.33 | 511.0446 |  | 560 | 617.7606 | 511.0446
18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 145.25 | 158 | 163.2193 |  | 165 | 215.5092 | 163.2193
19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 24.9 | 26.6 | 26.8902 |  | 27 | 57.6389 | 26.8902
20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日1/4の自然室温（Case 600FF）
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -13.04 | -12.02 | -10.4574 | -12.62 | -11.63 | -11.8 | -10.4574
2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -14.59 | -13.5 | -12.1092 | -14.27 | -13.48 | -13.4 | -12.1092
3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -15.65 | -14.7 | -13.5291 | -15.73 | -14.97 | -14.6 | -13.5291
4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -16.46 | -15.65 | -14.66 | -16.89 | -16.21 | -15.5 | -14.66
5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -17.16 | -16.47 | -15.627 | -17.88 | -17.27 | -16.4 | -15.627
6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.79 | -17.14 | -16.4432 | -18.71 | -18.18 | -17.1 | -16.4432
7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -18.32 | -17.7 | -17.1544 | -19.43 | -18.96 | -17.7 | -17.1544
8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -18.47 | -17.59 | -17.5283 | -19.99 | -19.56 | -17.7 | -17.5283
9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -15.47 | -13.46 | -14.9139 | -18.51 | -16.89 | -14.5 | -14.9139
10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -9.56 | -7.099 | -8.3575 | -13.56 | -11.24 | -8 | -8.3575
11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 0.49 | 3.657 | 1.3922 | -4.94 | -1.83 | 2.2 | 1.3922
12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 10.39 | 13.49 | 12.127 | 5.81 | 8.28 | 13 | 12.127
13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 18.75 | 21.77 | 21.2022 | 15.65 | 17.31 | 22.4 | 21.2022
14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 25.48 | 28.26 | 28.0199 | 23.54 | 24.69 | 30 | 28.0199
15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 29.21 | 32.09 | 32.1284 | 28.66 | 29.19 | 34.5 | 32.1284
16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 28.97 | 32.16 | 32.5897 | 30.21 | 30.2 | 35 | 32.5897
17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 22.58 | 25.71 | 28.2043 | 27.08 | 26.67 | 28.8 | 28.2043
18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 15.59 | 18.84 | 21.6872 | 20.81 | 21.04 | 21.5 | 21.6872
19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 10.2 | 13.1 | 15.9032 | 14.66 | 15.63 | 15.2 | 15.9032
20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 6.02 | 8.408 | 11.3558 | 9.46 | 10.98 | 10.1 | 11.3558
21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 2.39 | 4.387 | 7.0507 | 5.08 | 6.91 | 5.8 | 7.0507
22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | -0.59 | 0.9659 | 3.5836 | 1.39 | 3.46 | 2.2 | 3.5836
23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -3.04 | -1.781 | 0.6257 | -1.66 | 0.56 | -0.7 | 0.6257
24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -5.14 | -4.032 | -1.6964 | -4.24 | -1.95 | -3.2 | -1.6964
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日1/4の自然室温（Case 900FF）
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -2.68 | -3.455 | 0.72643 | -0.76 | -0.38 | 0.6 | 0.72643
2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.33 | -3.986 | 0.066993 | -1.4 | -1.09 | 0 | 0.066993
3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -3.72 | -4.395 | -0.45923 | -1.96 | -1.64 | -0.5 | -0.45923
4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.1 | -4.8 | -0.93674 | -2.45 | -2.18 | -1 | -0.93674
5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -4.51 | -5.216 | -1.446 | -2.94 | -2.71 | -1.5 | -1.446
6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -4.93 | -5.604 | -1.917 | -3.43 | -3.23 | -2 | -1.917
7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.34 | -5.984 | -2.3775 | -3.9 | -3.73 | -2.5 | -2.3775
8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -5.64 | -6.078 | -2.6597 | -4.35 | -4.21 | -2.8 | -2.6597
9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.59 | -4.717 | -1.649 | -3.81 | -3.61 | -2.2 | -1.649
10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.64 | -2.977 | 0.11787 | -2.16 | -2.22 | -0.7 | 0.11787
11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.75 | 0.2494 | 2.9923 | 0.43 | 0.18 | 1.7 | 2.9923
12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 3.26 | 2.539 | 5.4989 | 3.2 | 2.55 | 4.1 | 5.4989
13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.99 | 4.382 | 7.5557 | 5.1 | 4.63 | 6.2 | 7.5557
14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 6.51 | 5.853 | 9.2184 | 6.5 | 6.46 | 8 | 9.2184
15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 7.11 | 6.614 | 10.0725 | 7.21 | 7.51 | 9.1 | 10.0725
16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.68 | 6.333 | 9.8618 | 7.02 | 7.75 | 9.4 | 9.8618
17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.24 | 4.204 | 8.3893 | 5.58 | 6.84 | 8 | 8.3893
18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.45 | 2.869 | 6.8932 | 3.94 | 5.6 | 6.8 | 6.8932
19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 1.71 | 2.107 | 5.8967 | 3.1 | 4.73 | 6 | 5.8967
20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.32 | 1.581 | 5.1931 | 2.51 | 4.08 | 5.2 | 5.1931
21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 0.82 | 1.047 | 4.5093 | 1.97 | 3.44 | 4.5 | 4.5093
22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.42 | 0.5504 | 3.8845 | 1.46 | 2.89 | 3.9 | 3.8845
23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.05 | 0.1517 | 3.3882 | 1 | 2.38 | 3.4 | 3.3882
24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.34 | -0.238 | 2.8999 | 0.52 | 1.87 | 2.8 | 2.8999
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日7/27の自然室温（Case 650FF）
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.26 | 22.69 | 22.8217 | 23.65 | 22.39 | 22.5 | 22.8217
2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.11 | 21.33 | 21.3196 | 21.93 | 21 | 21.3 | 21.3196
3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.28 | 20.41 | 20.3591 | 20.74 | 20 | 20.4 | 20.3591
4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.49 | 19.61 | 19.5402 | 19.8 | 19.16 | 19.6 | 19.5402
5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.14 | 19.16 | 19.0164 | 19.14 | 18.74 | 19.2 | 19.0164
6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.81 | 19.6 | 19.3361 | 19.2 | 19.23 | 19.8 | 19.3361
7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 22.49 | 21.68 | 21.4065 | 20.78 | 21.6 | 22.2 | 21.4065
8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 24.81 | 23.47 | 23.8142 | 23.45 | 23.39 | 24.1 | 23.8142
9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 28.04 | 26.38 | 26.7262 | 26.87 | 26.39 | 27.4 | 26.7262
10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 32.11 | 30.35 | 31.098 | 31.42 | 30.22 | 31.7 | 31.098
11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 36.54 | 34.82 | 35.2234 | 36.61 | 34.58 | 36.5 | 35.2234
12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 41.15 | 39.38 | 39.8887 | 41.87 | 39.1 | 41.5 | 39.8887
13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 45.03 | 43.48 | 43.9853 | 46.51 | 43.21 | 45.8 | 43.9853
14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 47.65 | 46.14 | 47.0105 | 49.91 | 46.41 | 49 | 47.0105
15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 49.04 | 47.4 | 48.5663 | 51.61 | 48.24 | 50.6 | 48.5663
16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 49.28 | 47.33 | 48.7038 | 51.63 | 48.53 | 50.7 | 48.7038
17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 48.73 | 46.71 | 47.9863 | 50.73 | 47.99 | 50 | 47.9863
18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 46.58 | 45.28 | 46.5822 | 49.32 | 46.68 | 39.9 | 46.5822
19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 34.91 | 33.1 | 35.2501 | 43.01 | 36.59 | 34.4 | 35.2501
20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.69 | 30.49 | 31.7499 | 35.46 | 32.33 | 31.1 | 31.7499
21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.81 | 28.55 | 29.3277 | 31.82 | 29.54 | 28.8 | 29.3277
22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 27.1935 | 28.97 | 27.12 | 26.6 | 27.1935
23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.69 | 25.55 | 25.786 | 26.94 | 25.87 | 25.7 | 25.786
24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.1 | 24.26 | 24.4787 | 25.35 | 24.22 | 24.1 | 24.4787
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日7/27の自然室温（Case 950FF）
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 24.53 | 25.28 | 24.5751 | 26.15 | 24.75 | 25.2 | 24.5751
2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 23.8 | 24.47 | 23.6613 | 25.23 | 23.99 | 24.5 | 23.6613
3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.23 | 23.87 | 23.0488 | 24.58 | 23.36 | 23.8 | 23.0488
4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 22.6 | 23.26 | 22.4362 | 23.96 | 22.71 | 23.2 | 22.4362
5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.27 | 22.87 | 22.0084 | 23.46 | 22.33 | 22.8 | 22.0084
6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 22.67 | 23.06 | 22.1691 | 23.41 | 22.56 | 23.1 | 22.1691
7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.55 | 24.38 | 23.5666 | 24.34 | 24.08 | 24.7 | 23.5666
8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.57 | 27.21 | 26.76 | 26.26 | 25.73 | 26.9 | 26.76
9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 29.42 | 27.98 | 28.5614 | 28.05 | 26.84 | 27.8 | 28.5614
10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 30.68 | 29.11 | 30.0275 | 29.43 | 27.97 | 28.9 | 30.0275
11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 31.91 | 30.31 | 31.2247 | 30.82 | 29.17 | 30.1 | 31.2247
12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 33.27 | 31.53 | 32.3606 | 32.13 | 30.43 | 31.4 | 32.3606
13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 34.27 | 32.55 | 33.3769 | 33.21 | 31.54 | 32.5 | 33.3769
14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 34.9 | 33.15 | 34.0279 | 33.89 | 32.44 | 33.3 | 34.0279
15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 35.19 | 33.37 | 34.3675 | 34.13 | 32.95 | 33.8 | 34.3675
16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 35.28 | 33.38 | 34.4082 | 34.05 | 33.05 | 34 | 34.4082
17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 35.3 | 33.37 | 34.3767 | 34 | 33.03 | 34.2 | 34.3767
18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 34.71 | 33.16 | 34.094 | 33.94 | 32.81 | 32 | 34.094
19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.74 | 30.43 | 30.5381 | 32.53 | 30.57 | 30.8 | 30.5381
20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.38 | 29.61 | 29.4096 | 30.78 | 29.59 | 29.9 | 29.4096
21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 27.64 | 28.89 | 28.5729 | 29.94 | 28.78 | 29.1 | 28.5729
22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.46 | 27.93 | 27.5311 | 29.04 | 27.69 | 28 | 27.5311
23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.1 | 27.42 | 26.8874 | 28.34 | 27.31 | 27.6 | 26.8874
24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.02 | 26.59 | 26.0901 | 27.64 | 26.27 | 26.5 | 26.0901
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日1/4の冷暖房負荷（Case 600）
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 4.225 | 3.7667 | 3.5735 | 3.864 | 4.199 | 3.9069 | 3.5735
2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 4.354 | 3.8667 | 3.693 | 3.9888 | 4.3411 | 4.0186 | 3.693
3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 4.321 | 3.9028 | 3.7311 | 4.0512 | 4.3282 | 4.072 | 3.7311
4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 4.308 | 3.8944 | 3.7401 | 4.0464 | 4.309 | 4.0488 | 3.7401
5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 4.303 | 3.9167 | 3.7518 | 4.0416 | 4.2979 | 4.0441 | 3.7518
6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 4.307 | 3.9306 | 3.7479 | 4.0368 | 4.2912 | 4.0453 | 3.7479
7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 4.307 | 3.9306 | 3.7478 | 4.0368 | 4.2835 | 4.0465 | 3.7478
8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 4.167 | 3.7528 | 3.5211 | 4.0224 | 4.2418 | 3.9976 | 3.5211
9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.912 | 2.4228 | 2.1269 | 3.2208 | 2.6179 | 3.3383 | 2.1269
10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 1.466 | 0.79667 | 0.59941 | 1.4448 | 0.5064 | 1.4128 | 0.59941
11 | 0.151 | 0 | 0 | 0 |  | 0 | 0 | -0.034833 | -0.071877 | 0.2304 | 0 | -0.046511 | -0.071877
12 | -0.771 | -1.2242 | -1.552 | -1.066 |  | -1.036 | -0.424 | -1.435 | -1.9509 | -1.1664 | -2.0942 | -0.99883 | -1.9509
13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.364 | -2.7203 | -3.354 | -2.8992 | -3.8261 | -3.1174 | -3.354
14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -2.759 | -3.1556 | -3.6172 | -3.504 | -4.1261 | -3.8918 | -3.6172
15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.431 | -2.8444 | -2.9636 | -3.072 | -3.3293 | -3.7709 | -2.9636
16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.14 | -1.7158 | -1.473 | -1.7856 | -1.6906 | -2.7186 | -1.473
17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | -0.020536 | -0.48 | 0 | -0.59418 | -0.020536
18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 1.292 | 0.77306 | 0.4236 | 0.8112 | 0.07872 | 0.21395 | 0.4236
19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.445 | 2.3014 | 1.8281 | 2.3184 | 2.6616 | 2.0023 | 1.8281
20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.941 | 2.9667 | 2.571 | 3.2304 | 3.3298 | 2.986 | 2.571
21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.405 | 3.2778 | 2.9766 | 3.5328 | 3.6158 | 3.3116 | 2.9766
22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.594 | 3.4611 | 3.1881 | 3.6192 | 3.6979 | 3.486 | 3.1881
23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.696 | 3.5 | 3.2464 | 3.6192 | 3.6998 | 3.5418 | 3.2464
24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.769 | 3.4722 | 3.2643 | 3.6144 | 3.7027 | 3.5581 | 3.2643
= | = | = | = | = | = | = | = | = | = | = | = | =
代表日1/4の冷暖房負荷（Case 900）
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | = | = | = | =
1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.4 | 3.0806 | 2.6854 | 3.2112 | 3.3941 | 3.1709 | 2.6854
2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.547 | 3.2028 | 2.8295 | 3.36 | 3.575 | 3.3093 | 2.8295
3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.573 | 3.2778 | 2.9046 | 3.456 | 3.6413 | 3.4011 | 2.9046
4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.629 | 3.3306 | 2.9825 | 3.5136 | 3.7205 | 3.4523 | 2.9825
5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.687 | 3.4167 | 3.0606 | 3.5712 | 3.7925 | 3.5128 | 3.0606
6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.747 | 3.4694 | 3.1168 | 3.6288 | 3.8544 | 3.5686 | 3.1168
7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.797 | 3.5167 | 3.1744 | 3.6768 | 3.9067 | 3.6186 | 3.1744
8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.794 | 3.4639 | 3.0928 | 3.7104 | 3.947 | 3.65 | 3.0928
9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 3.168 | 2.8333 | 2.4636 | 3.2112 | 3.2842 | 3.4604 | 2.4636
10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.449 | 2.0561 | 1.7848 | 2.2176 | 2.3232 | 2.7686 | 1.7848
11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 1.293 | 0.79333 | 0.99823 | 0.888 | 0.91248 | 1.6442 | 0.99823
12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.619 | 0.037278 | 0.27993 | 0.0192 | 0 | 0.36162 | 0.27993
13 | 0.074 | 0 | 0 | 0 |  | 0 | 0.136 | 0 | 0 | 0 | 0 | -0.025581 | 0
14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | -0.024418 | 0
15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | -0.012791 | 0
16 | 0 | 0 | 0 | 0 |  | 0 | 0.088 | 0 | 0 | 0 | 0 | 0.0011628 | 0
17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 1.198 | 0.13494 | 0.12595 | 0.1488 | 0 | 0.027907 | 0.12595
18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 1.602 | 0.76444 | 0.61859 | 0.6384 | 0 | 0.026744 | 0.61859
19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.805 | 1.1986 | 0.98405 | 1.1616 | 0.48192 | 0.13488 | 0.98405
20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.943 | 1.4589 | 1.2301 | 1.4784 | 0.99264 | 0.67906 | 1.2301
21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 2.121 | 1.7008 | 1.4598 | 1.7472 | 1.3944 | 1.1442 | 1.4598
22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 2.227 | 1.9342 | 1.6442 | 1.9776 | 1.6973 | 1.5291 | 1.6442
23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.338 | 2.0922 | 1.757 | 2.1648 | 1.9522 | 1.8256 | 1.757
24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.458 | 2.2267 | 1.8519 | 2.3376 | 2.1898 | 2.0767 | 1.8519
= | = | = | = | = | = | = | = | = | = |  | = | =
自然室温頻度分布（Case 900FF）
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
= | = | = | = | = | = | = | = | = | = | = | = | =
-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0
-5 | 0 | 0 | 1 | 2 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 0 | 0
-4 | 0 | 1 | 3 | 3 | 4 | 4 | 5 | 6 | 0 | 3 | 1 | 0 | 0
-3 | 0 | 3 | 7 | 5 | 2 | 3 | 7 | 6 | 2 | 4 | 3 | 1 | 2
-2 | 3 | 5 | 5 | 7 | 7 | 8 | 10 | 12 | 5 | 6 | 7 | 3 | 5
-1 | 3 | 6 | 10 | 7 | 5 | 5 | 18 | 13 | 6 | 9 | 4 | 5 | 6
0 | 8 | 10 | 18 | 19 | 18 | 18 | 20 | 12 | 7 | 11 | 8 | 6 | 7
1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 15 | 18 | 16 | 11 | 15
2 | 18 | 14 | 18 | 13 | 20 | 14 | 16 | 20 | 14 | 14 | 16 | 16 | 14
3 | 18 | 19 | 19 | 15 | 15 | 19 | 25 | 18 | 18 | 18 | 18 | 17 | 18
4 | 17 | 14 | 20 | 23 | 20 | 21 | 24 | 20 | 16 | 18 | 16 | 15 | 16
5 | 18 | 25 | 30 | 28 | 24 | 27 | 27 | 26 | 21 | 25 | 20 | 17 | 21
6 | 22 | 19 | 25 | 29 | 27 | 30 | 35 | 34 | 24 | 38 | 29 | 23 | 24
7 | 31 | 33 | 37 | 28 | 28 | 33 | 45 | 29 | 32 | 34 | 27 | 28 | 32
8 | 30 | 34 | 51 | 46 | 33 | 46 | 59 | 44 | 29 | 36 | 32 | 25 | 29
9 | 42 | 42 | 59 | 62 | 57 | 61 | 73 | 55 | 44 | 55 | 44 | 34 | 44
10 | 51 | 54 | 84 | 69 | 53 | 71 | 118 | 57 | 56 | 73 | 56 | 47 | 56
11 | 67 | 72 | 107 | 111 | 89 | 116 | 134 | 95 | 63 | 89 | 68 | 51 | 63
12 | 90 | 115 | 139 | 137 | 112 | 127 | 138 | 127 | 98 | 109 | 95 | 72 | 98
13 | 115 | 137 | 153 | 141 | 142 | 157 | 173 | 143 | 114 | 136 | 117 | 96 | 114
14 | 156 | 159 | 158 | 154 | 151 | 160 | 183 | 162 | 143 | 164 | 141 | 111 | 143
15 | 172 | 165 | 206 | 188 | 178 | 207 | 234 | 183 | 167 | 189 | 150 | 147 | 167
16 | 215 | 198 | 239 | 232 | 195 | 224 | 274 | 234 | 187 | 197 | 178 | 153 | 187
17 | 244 | 245 | 274 | 253 | 248 | 255 | 298 | 273 | 230 | 242 | 210 | 182 | 230
18 | 293 | 277 | 350 | 301 | 266 | 315 | 342 | 296 | 268 | 275 | 251 | 207 | 268
19 | 338 | 317 | 322 | 336 | 332 | 347 | 352 | 356 | 322 | 302 | 316 | 250 | 322
20 | 387 | 365 | 375 | 342 | 344 | 352 | 331 | 346 | 335 | 342 | 330 | 317 | 335
21 | 398 | 358 | 392 | 362 | 361 | 366 | 334 | 388 | 367 | 370 | 347 | 339 | 367
22 | 385 | 372 | 364 | 329 | 376 | 349 | 343 | 380 | 383 | 332 | 397 | 327 | 383
23 | 396 | 341 | 370 | 348 | 366 | 357 | 349 | 366 | 395 | 331 | 381 | 380 | 395
24 | 380 | 368 | 381 | 352 | 341 | 341 | 338 | 401 | 369 | 342 | 351 | 377 | 369
25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 410 | 354 | 397 | 351 | 410
26 | 455 | 389 | 431 | 373 | 426 | 399 | 393 | 436 | 406 | 359 | 401 | 391 | 406
27 | 459 | 420 | 415 | 415 | 418 | 403 | 396 | 465 | 464 | 395 | 444 | 397 | 464
28 | 445 | 463 | 452 | 390 | 446 | 440 | 411 | 412 | 434 | 439 | 454 | 429 | 434
29 | 459 | 419 | 410 | 405 | 432 | 396 | 391 | 408 | 444 | 431 | 431 | 455 | 444
30 | 415 | 396 | 404 | 418 | 422 | 395 | 362 | 398 | 448 | 384 | 432 | 446 | 448
31 | 406 | 393 | 342 | 401 | 389 | 360 | 342 | 335 | 405 | 412 | 400 | 415 | 405
32 | 369 | 348 | 349 | 341 | 334 | 337 | 322 | 348 | 357 | 347 | 373 | 404 | 357
33 | 339 | 315 | 309 | 330 | 338 | 306 | 291 | 310 | 336 | 328 | 329 | 357 | 336
34 | 277 | 321 | 242 | 285 | 311 | 306 | 266 | 297 | 316 | 346 | 330 | 320 | 316
35 | 230 | 303 | 197 | 246 | 262 | 256 | 210 | 202 | 253 | 289 | 264 | 337 | 253
36 | 191 | 254 | 185 | 213 | 203 | 217 | 169 | 197 | 198 | 247 | 235 | 285 | 198
37 | 164 | 195 | 136 | 156 | 189 | 166 | 151 | 161 | 190 | 217 | 214 | 236 | 190
38 | 108 | 175 | 92 | 146 | 137 | 138 | 132 | 97 | 132 | 161 | 148 | 191 | 132
39 | 71 | 99 | 74 | 112 | 103 | 97 | 85 | 86 | 106 | 123 | 122 | 173 | 106
40 | 37 | 66 | 35 | 90 | 71 | 57 | 59 | 48 | 73 | 82 | 85 | 116 | 73
41 | 15 | 32 | 16 | 58 | 35 | 31 | 32 | 22 | 39 | 41 | 45 | 91 | 39
42 | 0 | 25 | 5 | 36 | 18 | 10 | 20 | 11 | 16 | 22 | 22 | 63 | 16
43 | 0 | 5 | 0 | 18 | 5 | 1 | 1 | 2 | 3 | 1 | 5 | 31 | 3
44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
= | = | = | = | = | ======== | = | = | = | = | = | = | =
= | = | = | = | = | ======== | = | = | = | = | = | = | =
= | = | = | = | = | = | = | = | = | = | = | = | =
= | = | = | = | = | = | = | = | = | = | = | = | =
複数室
冷房負荷
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW | kW
MZN | [8 empty] | 1.5413 | 1.3104 | 1.3272 | 1.3337 | 1.5415 | SHASE_G独自ケース
MZA | [9 empty] | 3.12 | 3.3005 | 4.1767 | 3.118 | SHASE_G独自ケース
室温
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | FINLAND | BEL/UK | USA | JAPAN | JAPAN | JAPAN
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
MZN_Zone A | [8 empty] | 31.06 | 30.89 | 32.62 | 33 | 31.0587 | SHASE_G独自ケース
MZN_Zone B | [8 empty] | 24.8 | 24.7 | 25.62 | 25.8 | 24.7984 | SHASE_G独自ケース
MZN_Zone C | [8 empty] | 15 | 15 | 15 | 15 | 15 | SHASE_G独自ケース
MZA_Zone A | [9 empty] | 23.44 | 25.2 | 21.82 | 25.7323 | SHASE_G独自ケース
MZA_Zone B | [9 empty] | 20.1 | 21.15 | 18.89 | 21.4658 | SHASE_G独自ケース
MZA_Zone C | [9 empty] | 15 | 15 | 15 | 15 | SHASE_G独自ケース

## グラフ_抜粋
計算結果グラフ一覧
■単室－基本テスト：小熱容量
■単室－基本テスト：大熱容量1
■単室－基本テスト：大熱容量2
■単室－詳細テスト：Aルート
■単室－詳細テスト：Bルート
■自然室温
■日射量
■代表日冷暖房負荷
■複数室

## グラフ_全て
計算結果グラフ一覧
■単室－基本テスト：小熱容量
■単室－基本テスト：大熱容量1
■単室－基本テスト：大熱容量2
■単室－詳細テスト：Aルート
■単室－詳細テスト：Bルート
■自然室温
■日射量
■代表日冷暖房負荷
■複数室

## グラフ_抜粋_ガイドライン
計算結果グラフ一覧
■単室－基本テスト：小熱容量
■単室－基本テスト：大熱容量1
■単室－基本テスト：大熱容量2
■単室－詳細テスト：Aルート
■単室－詳細テスト：Bルート
■自然室温
■日射量
■代表日冷暖房負荷
■複数室

## グラフ_全て_ガイドライン
計算結果グラフ一覧
■単室－基本テスト：小熱容量
■単室－基本テスト：大熱容量1
■単室－基本テスト：大熱容量2
■単室－詳細テスト：Aルート
■単室－詳細テスト：Bルート
■自然室温
■日射量
■代表日冷暖房負荷
■複数室

## グラフ用データ整理 (hidden)
※本シートは記入する必要はありません！
■単室－基本テスト：小熱容量
年間の暖房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 5.362 | 4.872 | 4.3871 | 5.4524 | 5.6857 | 4.994 | 4.3871
| 610 | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 5.383 | 4.97 | 4.4299 | 5.4888 | 5.8263 | 5.2341 | 4.4299
| 620 | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.728 | 5.073 | 4.5646 | 5.6118 | 5.8848 | 5.2042 | 4.5646
| 630 | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 0 | 5.624 | 4.8942 | 6.0366 | 6.5356 | 5.7664 | 4.8942
| 640 | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.309 | 3.043 | 2.6948 | 0 | 4.0695 | 2.5382 | 2.6948
| 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 0 | 0.019809 | 0
年間の冷房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.778 | 6.492 | 6.7453 | 7.2655 | 7.4541 | 7.9057 | 6.7453
| 610 | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 5.506 | 4.601 | 4.7484 | 4.9042 | 4.6982 | 4.2928 | 4.7484
| 620 | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 4.351 | 3.901 | 4.1709 | 4.5636 | 4.6445 | 5.1056 | 4.1709
| 630 | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 0 | 2.416 | 2.7837 | 2.6439 | 2.3089 | 3.0834 | 2.7837
| 640 | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.508 | 6.246 | 6.4599 | 0 | 7.3367 | 7.7112 | 6.4599
| 650 | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.456 | 5.119 | 5.3035 | 5.7031 | 5.6459 | 6.3344 | 5.3035
最大暖房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 3.437 | 3.94 | 4.045 | 4.258 | 0 | 4.037 | 4.354 | 3.9306 | 3.7518 | 4.0512 | 4.3411 | 4.072 | 3.7518
| 610 | 3.437 | 3.941 | 4.034 | 4.258 | 0 | 4.037 | 4.354 | 3.9222 | 3.7413 | 4.032 | 4.3272 | 4.079 | 3.7413
| 620 | 3.591 | 3.941 | 4.046 | 4.277 | 0 | 4.277 | 4.379 | 3.9222 | 3.7411 | 4.0512 | 4.343 | 4.0895 | 3.7411
| 630 | 3.592 | 3.941 | 4.025 | 4.28 | 0 | 4.278 | 0 | 3.9222 | 3.7209 | 4.0224 | 4.3166 | 4.0918 | 3.7209
| 640 | 5.232 | 5.486 | 5.943 | 6.53 | 0 | 6.347 | 6.954 | 5.7222 | 6.3682 | 0 | 8.376 | 6.7569 | 6.3682
| 650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
最大冷房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.194 | 5.965 | 6.656 | 6.827 | 0 | 6.286 | 6.812 | 6.4861 | 6.5686 | 6.4608 | 7.0992 | 7.0895 | 6.5686
| 610 | 5.669 | 5.824 | 6.064 | 6.371 | 0 | 6.17 | 6.146 | 5.675 | 6.1674 | 6.2688 | 6.6312 | 5.7639 | 6.1674
| 620 | 3.634 | 4.075 | 4.43 | 4.593 | 0 | 4.297 | 5.096 | 4.275 | 3.9234 | 4.224 | 4.4573 | 5.043 | 3.9234
| 630 | 3.072 | 3.704 | 3.588 | 4.116 | 0 | 3.665 | 0 | 3.6083 | 3.3784 | 3.5856 | 3.4166 | 4.1209 | 3.3784
| 640 | 6.161 | 5.892 | 6.576 | 6.776 | 0 | 6.25 | 6.771 | 6.4417 | 6.5043 | 0 | 7.0838 | 7.0604 | 6.5043
| 650 | 6.031 | 5.831 | 6.516 | 6.671 | 0 | 6.143 | 6.679 | 6.3778 | 6.3742 | 6.3648 | 6.9163 | 6.9499 | 6.3742
■単室－基本テスト：大熱容量1
年間の暖房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 5.362 | 4.872 | 4.3871 | 5.4524 | 5.6857 | 4.994 | 4.3871
| 900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 2.041 | 1.655 | 1.2286 | 1.7867 | 1.822 | 1.5153 | 1.2286
| 960 | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 2.816 | 3.373 | 2.4329 | 3.7485 | 3.5112 | 2.2663 | 2.4329
| 900-J1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9854 | 3.0063 | 2.4214 | 2.6889 | 1.9854
| 900-J1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0803 | 4.1845 | 3.9625 | 3.9379 | 3.0803
| 900-J2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0566 | 1.5934 | 1.6905 | 1.8167 | 1.0566
| 900-J3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4785 | 5.3524 | 5.4406 | 5.7973 | 5.4785
年間の冷房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.778 | 6.492 | 6.7453 | 7.2655 | 7.4541 | 7.9057 | 6.7453
| 900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.599 | 2.485 | 2.5112 | 2.7841 | 2.7647 | 3.4899 | 2.5112
| 960 | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.786 | 0.4113 | 0.63915 | 0.19589 | 0.37033 | 0.6552 | 0.63915
| 900-J1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5402 | 4.3178 | 4.214 | 3.9287 | 3.5402
| 900-J1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6184 | 2.115 | 2.2312 | 2.0794 | 1.6184
| 900-J2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.337 | 1.7128 | 1.8256 | 1.6662 | 1.337
| 900-J3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49076 | 1.3251 | 1.4425 | 1.0287 | 0.49076
最大暖房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 3.437 | 3.94 | 4.045 | 4.258 | 0 | 4.037 | 4.354 | 3.9306 | 3.7518 | 4.0512 | 4.3411 | 4.072 | 3.7518
| 900 | 2.85 | 3.453 | 3.557 | 3.76 | 0 | 3.608 | 3.797 | 3.5167 | 3.1744 | 3.7104 | 3.947 | 3.65 | 3.1744
| 960 | 2.41 | 2.751 | 2.727 | 2.863 | 0 | 2.852 | 2.779 | 2.522 | 2.7006 | 2.2464 | 2.797 | 2.6349 | 2.7006
| 900-J1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4047 | 3.8688 | 3.9432 | 3.9348 | 3.4047
| 900-J1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2401 | 4.6512 | 5.1082 | 4.8453 | 4.2401
| 900-J2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1306 | 10.1232 | 11.3803 | 9.1232 | 7.1306
| 900-J3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5872 | 4.7712 | 5.1158 | 5.0453 | 4.5872
最大冷房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.194 | 5.965 | 6.656 | 6.827 | 0 | 6.286 | 6.812 | 6.4861 | 6.5686 | 6.4608 | 7.0992 | 7.0895 | 6.5686
| 900 | 2.888 | 3.155 | 3.458 | 3.871 | 0 | 3.334 | 3.457 | 3.5667 | 3.2552 | 3.4128 | 3.8707 | 4.0907 | 3.2552
| 960 | 0.953 | 1.144 | 1.057 | 1.37 | 0 | 1.179 | 1.403 | 1.378 | 1.1419 | 0.8592 | 1.0411 | 0.99999 | 1.1419
| 900-J1-1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0622 | 4.3392 | 4.4597 | 3.9988 | 4.0622
| 900-J1-2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6921 | 3.3552 | 3.445 | 3.2569 | 2.6921
| 900-J2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8468 | 3.456 | 3.6197 | 3.4151 | 2.8468
| 900-J3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5426 | 2.9424 | 3.1723 | 2.693 | 1.5426
■単室－基本テスト：大熱容量2
年間の暖房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 2.041 | 1.655 | 1.2286 | 1.7867 | 1.822 | 1.5153 | 1.2286
| 910 | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.22 | 2.097 | 1.5109 | 2.1821 | 2.6713 | 2.4018 | 1.5109
| 920 | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 4.3 | 3.776 | 3.2088 | 3.9527 | 4.782 | 3.6631 | 3.2088
| 930 | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 0 | 4.74 | 3.9205 | 4.9414 | 6.0858 | 4.7328 | 3.9205
| 940 | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.323 | 1.08 | 0.77258 | 0 | 1.5307 | 1.0648 | 0.77258
| 950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 0 | 0.02043 | 0
年間の冷房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.599 | 2.485 | 2.5112 | 2.7841 | 2.7647 | 3.4899 | 2.5112
| 910 | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.767 | 1.326 | 1.2354 | 1.2058 | 0.67341 | 1.166 | 1.2354
| 920 | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.613 | 2.418 | 2.5522 | 2.6778 | 2.5272 | 3.3079 | 2.5522
| 930 | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 0 | 1.416 | 1.641 | 1.4385 | 1.1711 | 1.8763 | 1.641
| 940 | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.516 | 2.383 | 2.4368 | 0 | 2.091 | 3.3295 | 2.4368
| 950 | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.771 | 0.5606 | 0.53092 | 0.62267 | 0.48406 | 0.71387 | 0.53092
最大暖房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 900 | 2.85 | 3.453 | 3.557 | 3.76 | 0 | 3.608 | 3.797 | 3.5167 | 3.1744 | 3.7104 | 3.947 | 3.65 | 3.1744
| 910 | 2.858 | 3.456 | 3.564 | 3.764 | 0 | 3.618 | 3.801 | 3.5361 | 3.1742 | 3.7056 | 4.2302 | 3.7023 | 3.1742
| 920 | 3.308 | 3.703 | 3.805 | 4.013 | 0 | 4.029 | 4.061 | 3.7083 | 3.4842 | 3.84 | 4.4131 | 3.8267 | 3.4842
| 930 | 3.355 | 3.732 | 3.832 | 4.042 | 0 | 4.064 | 0 | 3.7444 | 3.5074 | 3.8448 | 4.4371 | 3.8825 | 3.5074
| 940 | 3.98 | 5.028 | 5.665 | 6.116 | 0 | 6.117 | 6.428 | 5.1222 | 4.8682 | 0 | 8.1427 | 6.3988 | 4.8682
| 950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
最大冷房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 900 | 2.888 | 3.155 | 3.458 | 3.871 | 0 | 3.334 | 3.457 | 3.5667 | 3.2552 | 3.4128 | 3.8707 | 4.0907 | 3.2552
| 910 | 1.896 | 2.5 | 2.336 | 3.277 | 0 | 2.786 | 3.147 | 2.7917 | 2.5779 | 2.664 | 2.459 | 2.107 | 2.5779
| 920 | 2.385 | 2.933 | 3.109 | 3.487 | 0 | 3.071 | 3.505 | 3.05 | 2.7822 | 3.2496 | 3.1848 | 3.7093 | 2.7822
| 930 | 1.873 | 2.546 | 2.388 | 3.08 | 0 | 2.486 | 0 | 2.4983 | 2.2789 | 2.6256 | 2.4528 | 2.9174 | 2.2789
| 940 | 2.888 | 3.155 | 3.458 | 3.871 | 0 | 3.334 | 3.457 | 3.5667 | 3.2551 | 0 | 3.4114 | 4.0907 | 3.2551
| 950 | 2.033 | 2.621 | 2.664 | 3.17 | 0 | 2.677 | 2.867 | 2.6861 | 2.3924 | 2.7792 | 3.0086 | 3.2209 | 2.3924
■単室－詳細テスト：Aルート
年間の暖房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 5.362 | 4.872 | 4.3871 | 5.4524 | 5.6857 | 4.994 | 4.3871
| 220 | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.437 | 7.297 | 7.115 | 8.5562 | 8.5586 | 7.7498 | 7.115
| 210 | 6.456 | 6.559 | 0 | 0 | 0 | 0 | 6.967 | 6.554 | 6.606 | 0 | 8.5586 | 7.1394 | 6.606
| 200 | 5.252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3154 | 0 | 7.834 | 7.0844 | 6.3154
| 195 | 4.167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6559 | 0 | 5.0239 | 5.0272 | 4.6559
| 215 | 5.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9495 | 7.6164 | 7.834 | 7.6898 | 5.9495
| 230 | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.964 | 10.84 | 10.9033 | 11.1587 | 12.0614 | 11.1882 | 10.9033
| 240 | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.234 | 6.076 | 5.8723 | 7.2242 | 7.9013 | 6.5127 | 5.8723
| 250 | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.738 | 5.764 | 5.195 | 6.8454 | 6.8145 | 6.2049 | 5.195
| 270 | 4.51 | 4.93 | 0 | 5.341 | 5.92 | 0 | 5.489 | 5.047 | 4.4786 | 0 | 5.7677 | 0 | 4.4786
年間の冷房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.778 | 6.492 | 6.7453 | 7.2655 | 7.4541 | 7.9057 | 6.7453
| 220 | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.683 | 0.7368 | 0.40633 | 0.51749 | 0.61323 | 0.77897 | 0.40633
| 210 | 0.162 | 0.613 | 0 | 0 | 0 | 0 | 0.641 | 0.6679 | 0.36507 | 0 | 0.61323 | 0.72191 | 0.36507
| 200 | 0.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43078 | 0 | 0.82213 | 0.73344 | 0.43078
| 195 | 0.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33399 | 0 | 0.52535 | 0.49803 | 0.33399
| 215 | 0.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64485 | 0.77043 | 0.82213 | 0.79184 | 0.64485
| 230 | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 0.985 | 1.04 | 0.69551 | 0.73616 | 0.91367 | 1.0744 | 0.69551
| 240 | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.045 | 1.114 | 0.70418 | 0.82602 | 0.80677 | 1.1629 | 0.70418
| 250 | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 3.38 | 2.684 | 3.1867 | 2.3813 | 2.7746 | 2.758 | 3.1867
| 270 | 7.528 | 8.67 | 0 | 9.828 | 10.35 | 0 | 8.714 | 8.764 | 8.1657 | 0 | 9.737 | 0 | 8.1657
最大暖房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 3.437 | 3.94 | 4.045 | 4.258 | 0 | 4.037 | 4.354 | 3.9306 | 3.7518 | 4.0512 | 4.3411 | 4.072 | 3.7518
| 220 | 2.867 | 3.28 | 3.465 | 3.695 | 0 | 3.348 | 3.52 | 3.3361 | 3.2464 | 3.6192 | 3.7003 | 3.5407 | 3.2464
| 210 | 2.701 | 2.973 | 0 | 0 | 0 | 0 | 3.325 | 2.9806 | 3.0445 | 0 | 3.7003 | 3.2628 | 3.0445
| 200 | 2.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9952 | 0 | 3.588 | 3.2616 | 2.9952
| 195 | 2.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1428 | 0 | 2.2906 | 2.286 | 2.1428
| 215 | 2.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0338 | 3.4704 | 3.588 | 3.5383 | 3.0338
| 230 | 4.386 | 4.984 | 4.994 | 5.279 | 0 | 5.159 | 5.107 | 4.8917 | 5.0669 | 4.7712 | 5.2622 | 5.0697 | 5.0669
| 240 | 2.685 | 3.1 | 3.282 | 3.495 | 0 | 3.159 | 3.333 | 3.1528 | 3.0628 | 3.432 | 3.6734 | 3.3558 | 3.0628
| 250 | 2.866 | 3.279 | 3.465 | 3.695 | 0 | 3.341 | 3.525 | 3.3361 | 3.2463 | 3.6192 | 3.7003 | 3.5395 | 3.2463
| 270 | 2.863 | 3.277 | 0 | 3.661 | 0 | 0 | 3.738 | 3.3361 | 3.0253 | 0 | 3.5885 | 0 | 3.0253
最大冷房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.194 | 5.965 | 6.656 | 6.827 | 0 | 6.286 | 6.812 | 6.4861 | 6.5686 | 6.4608 | 7.0992 | 7.0895 | 6.5686
| 220 | 0.56 | 1.166 | 0.937 | 1.34 | 0 | 1.215 | 1.213 | 1.1789 | 0.90998 | 1.0992 | 1.139 | 1.2465 | 0.90998
| 210 | 0.476 | 1.017 | 0 | 0 | 0 | 0 | 1.142 | 1.0678 | 0.81173 | 0 | 1.139 | 1.1442 | 0.81173
| 200 | 0.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8503 | 0 | 1.2998 | 1.1442 | 0.8503
| 195 | 0.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65384 | 0 | 0.83856 | 0.80348 | 0.65384
| 215 | 1.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.074 | 1.2288 | 1.2998 | 1.2477 | 1.074
| 230 | 1.059 | 1.646 | 1.455 | 1.875 | 0 | 1.7 | 1.749 | 1.7078 | 1.4067 | 1.4784 | 1.6517 | 1.7581 | 1.4067
| 240 | 0.739 | 1.347 | 1.119 | 1.54 | 0 | 1.398 | 1.397 | 1.3614 | 1.0927 | 1.2864 | 1.2523 | 1.4535 | 1.0927
| 250 | 3.36 | 3.036 | 2.605 | 2.59 | 0 | 2.258 | 4.912 | 3.2278 | 3.0393 | 2.2608 | 2.4634 | 2.4267 | 3.0393
| 270 | 6.356 | 6.641 | 0 | 7.234 | 0 | 0 | 6.867 | 6.7639 | 6.6298 | 0 | 7.4486 | 0 | 6.6298
■単室－詳細テスト：Bルート
年間の暖房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 5.362 | 4.872 | 4.3871 | 5.4524 | 5.6857 | 4.994 | 4.3871
| 400 | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.326 | 7.166 | 7.0274 | 8.4334 | 8.4001 | 7.6663 | 7.0274
| 395 | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.839 | 4.855 | 4.9843 | 5.5824 | 5.3929 | 4.9687 | 4.9843
| 410 | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 9.085 | 8.936 | 8.914 | 9.7274 | 10.1404 | 9.4149 | 8.914
| 420 | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.863 | 7.697 | 7.6559 | 8.3803 | 9.4607 | 8.1512 | 7.6559
| 430 | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.51 | 6.5 | 6.028 | 7.0951 | 7.983 | 6.9227 | 6.028
| 800 | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.861 | 5.94 | 6.4845 | 6.5324 | 7.6233 | 6.3488 | 6.4845
年間の冷房負荷 [MWh]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.778 | 6.492 | 6.7453 | 7.2655 | 7.4541 | 7.9057 | 6.7453
| 400 | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.044 | 0.04468 | 0.005787 | 0.0087888 | 0.011244 | 0.059988 | 0.005787
| 395 | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.011 | 0.01029 | 0.0004087 | 0.0006336 | 0.0010522 | 0.021577 | 0.0004087
| 410 | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.065 | 0.06707 | 0.016158 | 0.016954 | 0.025222 | 0.082013 | 0.016158
| 420 | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.143 | 0.1575 | 0.067594 | 0.071534 | 0.056398 | 0.17827 | 0.067594
| 430 | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.875 | 0.6174 | 0.65185 | 0.47298 | 0.43784 | 0.64355 | 0.65185
| 800 | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.325 | 0.2073 | 0.064574 | 0.10089 | 0.18422 | 0.2287 | 0.064574
最大暖房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 3.437 | 3.94 | 4.045 | 4.258 | 0 | 4.037 | 4.354 | 3.9306 | 3.7518 | 4.0512 | 4.3411 | 4.072 | 3.7518
| 400 | 2.867 | 3.28 | 3.476 | 3.695 | 0 | 3.342 | 3.52 | 3.3361 | 3.2464 | 3.6192 | 3.7003 | 3.5662 | 3.2464
| 395 | 2.062 | 2.209 | 2.328 | 2.385 | 0 | 2.263 | 2.27 | 2.2211 | 2.2333 | 2.3856 | 2.3674 | 2.3 | 2.2333
| 410 | 3.625 | 4.124 | 4.233 | 4.487 | 0 | 4.227 | 4.314 | 4.1139 | 4.1567 | 4.1952 | 4.4717 | 4.3453 | 4.1567
| 420 | 3.443 | 3.944 | 4.05 | 4.287 | 0 | 4.044 | 4.126 | 3.9306 | 3.973 | 4.008 | 4.4429 | 4.1593 | 3.973
| 430 | 3.442 | 3.944 | 4.05 | 4.287 | 0 | 4.044 | 4.137 | 3.9306 | 3.973 | 4.0032 | 4.4429 | 4.1581 | 3.973
| 800 | 3.227 | 3.793 | 3.909 | 4.138 | 0 | 3.902 | 3.939 | 3.7861 | 3.8183 | 3.8688 | 4.3877 | 4.0034 | 3.8183
最大冷房負荷 [kW]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600 | 6.194 | 5.965 | 6.656 | 6.827 | 0 | 6.286 | 6.812 | 6.4861 | 6.5686 | 6.4608 | 7.0992 | 7.0895 | 6.5686
| 400 | 0 | 0.581 | 0.265 | 0.666 | 0 | 0.612 | 0.572 | 0.61333 | 0.25475 | 0.4656 | 0.45648 | 0.64999 | 0.25475
| 395 | 0 | 0.362 | 0 | 0.394 | 0 | 0.356 | 0.345 | 0.3625 | 0.07329 | 0.2112 | 0.2064 | 0.37209 | 0.07329
| 410 | 0.035 | 0.699 | 0.413 | 0.814 | 0 | 0.724 | 0.71 | 0.74306 | 0.3952 | 0.5712 | 0.60864 | 0.79185 | 0.3952
| 420 | 0.258 | 0.923 | 0.631 | 1.047 | 0 | 0.938 | 0.921 | 0.93778 | 0.6316 | 0.8064 | 0.75024 | 1.0105 | 0.6316
| 430 | 1.493 | 1.772 | 1.427 | 1.762 | 0 | 1.575 | 2.578 | 1.7983 | 1.7304 | 1.512 | 1.5384 | 1.6791 | 1.7304
| 800 | 0.585 | 0.967 | 0.743 | 1.352 | 0 | 1.028 | 1.358 | 0.98278 | 0.52505 | 0.9168 | 1.237 | 1.1325 | 0.52505
■自然室温
自然室温最大値 [℃]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600FF | 64.929 | 65.11 | 69.5 | 68.6 | 0 | 64.9 | 65.25 | 65.25 | 65.275 | 64.88 | 64.74 | 69.5 | 65.275
| 900FF | 41.812 | 43.44 | 42.7 | 44.8 | 0 | 43 | 43.17 | 42.46 | 43.1725 | 42.65 | 42.66 | 44.5 | 43.1725
| 650FF | 63.236 | 63.45 | 68.2 | 67 | 0 | 63.3 | 63.82 | 63.74 | 63.4835 | 63.42 | 62.58 | 66.6 | 63.4835
| 950FF | 35.54 | 36.23 | 35.9 | 38.5 | 0 | 36.1 | 37.58 | 35.67 | 36.6456 | 35.57 | 35.36 | 36.6 | 36.6456
| 960 | 48.943 | 48.88 | 49 | 51 | 0 | 50.2 | 48.92 | 55.34 | 51.4704 | 55.86 | 53.98 | 55.4 | 51.4704
自然室温最小値 [℃]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600FF | -15.565 | -17.05 | -18.8 | -18 | 0 | -17.8 | -18.47 | -17.81 | -17.5283 | -19.99 | -19.56 | -17.7 | -17.5283
| 900FF | -1.647 | -3.15 | -4.3 | -4.5 | 0 | -4 | -5.64 | -6.38 | -2.6597 | -4.35 | -4.21 | -2.8 | -2.6597
| 650FF | -22.564 | -22.96 | -21.6 | -23 | 0 | -22.9 | -22.91 | -22.83 | -23.0439 | -23.25 | -23.4 | -22.9 | -23.0439
| 950FF | -19.484 | -20.04 | -18.6 | -19.7 | 0 | -20.2 | -19.96 | -19.34 | -20.3396 | -19.03 | -20.07 | -19.8 | -20.3396
| 960 | 2.729 | 1.63 | 3.9 | 3.1 | 0 | 1.4 | -0.39 | -2.82 | 2.1322 | -2.41 | 1.74 | 4.3 | 2.1322
自然室温平均値 [℃]
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 600FF | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.22 | 24.49 | 25.8015 | 25.3518 | 25.2127 | 26.7084 | 25.8015
| 900FF | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.45 | 24.47 | 25.9963 | 25.4076 | 25.2464 | 26.7685 | 25.9963
| 650FF | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 18.36 | 17.99 | 18.6305 | 19.3174 | 18.0921 | 18.6483 | 18.6305
| 950FF | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.64 | 14.53 | 14.4891 | 14.9374 | 13.8294 | 14.3331 | 14.4891
| 960 | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 26.43 | 28.96 | 28.7726 | 31.1696 | 30.3189 | 31.8204 | 28.7726
■日射量
Case 600 年間積算日射量 [MWh/m2]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| NORTH | 0.427 | 0 | 0.434 | 0.456 | 0.4073 | 0.457 | 0.453 | 0.3674 | 0.43213 | 0 | 0.43024 | 0.43215 | 0.43213
| EAST | 0.959 | 0 | 1.155 | 1.083 | 1.2173 | 1.082 | 0.962 | 1.101 | 1.1793 | 0 | 1.1735 | 1.0077 | 1.1793
| WEST | 1.086 | 0 | 1.079 | 1.003 | 0.8565 | 1.002 | 1.09 | 1.012 | 1.0405 | 0 | 1.0429 | 1.2005 | 1.0405
| SOUTH | 1.456 | 0 | 1.566 | 1.476 | 1.4677 | 1.474 | 1.468 | 1.522 | 1.545 | 0 | 1.5464 | 1.5376 | 1.545
| HORZ. | 1.797 | 0 | 1.831 | 1.832 | 1.8318 | 1.832 | 1.832 | 1.832 | 1.8401 | 0 | 1.8497 | 1.8318 | 1.8401
Case 600 年間積算透過日射量 [MWh/m2] と透過係数 [-]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
Unshaded | WEST | 732 | 0 | 735 | 689 | 562.96 | 642 | 706 | 661.67 | 674.319 | 0 | 0 | 800.6768 | 674.319
| SOUTH | 946 | 0 | 1051 | 962 | 954.3 | 926 | 914 | 984.17 | 980.3665 | 0 | 0 | 999.4199 | 980.3665
Shaded | WEST | 599 | 0 | 481 | 554 | 441.3 | 431 | 0 | 437.5 | 487.4921 | 0 | 0 | 530.4459 | 487.4921
| SOUTH | 785 | 0 | 831 | 803 | 774.86 | 757 | 809 | 782 | 787.8056 | 0 | 0 | 658.3534 | 787.8056
Window Transmissivity | WEST | 0.67403 | #DIV/0! | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.64771 | 0.65382 | 0.64806 | #DIV/0! | 0 | 0.66694 | 0.64806
| SOUTH | 0.64973 | #DIV/0! | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.62262 | 0.64663 | 0.63455 | #DIV/0! | 0 | 0.64998 | 0.63455
Overhang and Fin Shading | WEST | 0.18169 | #DIV/0! | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 1 | 0.33879 | 0.27706 | #DIV/0! | #DIV/0! | 0.3375 | 0.27706
| SOUTH | 0.17019 | #DIV/0! | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.11488 | 0.20542 | 0.19642 | #DIV/0! | #DIV/0! | 0.34126 | 0.19642
曇天日3/5の南面日射量（Case 600） [Wh/m2]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3 | 3.05 | 4.1392 |  | 3 | 2.0814 | 4.1392
| 8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.68 | 20.69 | 19.9066 |  | 21 | 19.6626 | 19.9066
| 9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 35.4789 |  | 39 | 38.3019 | 35.4789
| 10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.56 | 54.67 | 48.9837 |  | 55 | 54.5226 | 48.9837
| 11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 65.99 | 66.08 | 58.4496 |  | 66 | 66.476 | 58.4496
| 12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.74 | 71.92 | 63.7276 |  | 73 | 72.4876 | 63.7276
| 13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.3 | 72.42 | 63.4692 |  | 73 | 73.2434 | 63.4692
| 14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.38 | 66.53 | 57.1639 |  | 67 | 67.2434 | 57.1639
| 15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 54.8 | 55 | 46.1404 |  | 55 | 55.3599 | 46.1404
| 16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.84 | 38.94 | 31.7261 |  | 39 | 38.4879 | 31.7261
| 17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.46 | 20.52 | 15.6423 |  | 20 | 20.1858 | 15.6423
| 18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 0 | 3.05 | 2.6702 |  | 3 | 0 | 2.6702
| 19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
曇天日3/5の西面日射量（Case 600） [Wh/m2]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 3 | 2.99 | 4.1007 |  | 3 | 2.9767 | 4.1007
| 8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.15 | 20.17 | 19.5371 |  | 20 | 20.8835 | 19.5371
| 9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.9 | 37.92 | 34.5799 |  | 38 | 38.2903 | 34.5799
| 10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.15 | 53.17 | 47.8212 |  | 53 | 53.2087 | 47.8212
| 11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.4 | 64.39 | 56.9729 |  | 64 | 63.8598 | 56.9729
| 12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.95 | 69.89 | 61.3278 |  | 69 | 69.1039 | 61.3278
| 13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 71.16 | 70.75 | 61.4275 |  | 70 | 70.7667 | 61.4275
| 14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 66.02 | 65.69 | 56.2762 |  | 65 | 66.383 | 56.2762
| 15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.16 | 55.03 | 46.1267 |  | 55 | 55.7087 | 46.1267
| 16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.73 | 39.61 | 32.2501 |  | 39 | 39.0112 | 32.2501
| 17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.6 | 21.42 | 16.1236 |  | 21 | 19.6626 | 16.1236
| 18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 0 | 3.28 | 2.7155 |  | 3 | 0 | 2.7155
| 19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
晴天日7/27の南面日射量（Case 600） [Wh/m2]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.2 | 0.17 | 2.8637 |  | 0 | 0 | 2.8637
| 6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 25.7 | 27.01 | 35.6572 |  | 27 | 26.0578 | 35.6572
| 7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 62.1 | 63 | 90.2926 |  | 85 | 73.2317 | 90.2926
| 8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 107.47 | 71.22 | 136.1384 |  | 125 | 123.7196 | 136.1384
| 9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 232.33 | 187.72 | 256.058 |  | 240 | 257.5669 | 256.058
| 10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 349.16 | 314.17 | 377.0924 |  | 366 | 369.9726 | 377.0924
| 11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 430.22 | 404.44 | 449.9555 |  | 448 | 441.1463 | 449.9555
| 12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 459.85 | 443.61 | 468.97 |  | 467 | 461.1577 | 468.97
| 13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 462.28 | 452.5 | 458.4652 |  | 467 | 454.8438 | 458.4652
| 14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 404.57 | 400.56 | 395.7752 |  | 407 | 391.3561 | 395.7752
| 15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 319.26 | 316.94 | 298.2775 |  | 317 | 299.1013 | 298.2775
| 16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 193.61 | 188.89 | 170.2592 |  | 187 | 165.4517 | 170.2592
| 17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 132.3 | 86.03 | 80.3704 |  | 81 | 97.3129 | 80.3704
| 18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 76.6 | 69.78 | 52.387 |  | 62 | 61.7668 | 52.387
| 19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 18.05 | 17.61 | 15.1854 |  | 17 | 15.6742 | 15.1854
| 20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
晴天日7/27の西面日射量（Case 600） [Wh/m2]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.2 | 0.17 | 2.8637 |  | 0 | 0 | 2.8637
| 6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 25.7 | 27.01 | 35.6572 |  | 27 | 26.0578 | 35.6572
| 7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 62.1 | 63 | 90.2926 |  | 85 | 73.2317 | 90.2926
| 8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 72 | 71.22 | 128.8229 |  | 125 | 97.9408 | 128.8229
| 9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 92.6 | 85.58 | 146.3844 |  | 145 | 116.4289 | 146.3844
| 10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 112.8 | 98.03 | 152.7179 |  | 153 | 129.0218 | 152.7179
| 11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 136.75 | 109.14 | 149.8255 |  | 150 | 134.4985 | 149.8255
| 12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 150.9 | 113.06 | 142.658 |  | 140 | 133.4404 | 142.658
| 13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 382.5 | 235.17 | 257.4 |  | 230 | 347.1008 | 257.4
| 14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 576.81 | 453.89 | 457.0081 |  | 433 | 554.3427 | 457.0081
| 15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 744.52 | 652.5 | 616.3624 |  | 606 | 735.5267 | 616.3624
| 16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 807.29 | 762.78 | 668.525 |  | 691 | 830.5954 | 668.525
| 17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 541.68 | 568.33 | 511.0446 |  | 560 | 617.7606 | 511.0446
| 18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 145.25 | 158 | 163.2193 |  | 165 | 215.5092 | 163.2193
| 19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 24.9 | 26.6 | 26.8902 |  | 27 | 57.6389 | 26.8902
| 20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
| 24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0
代表日1/4の自然室温（Case 600FF） [℃]
| CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -13.04 | -12.02 | -10.4574 | -12.62 | -11.63 | -11.8 | -10.4574
| 2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -14.59 | -13.5 | -12.1092 | -14.27 | -13.48 | -13.4 | -12.1092
| 3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -15.65 | -14.7 | -13.5291 | -15.73 | -14.97 | -14.6 | -13.5291
| 4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -16.46 | -15.65 | -14.66 | -16.89 | -16.21 | -15.5 | -14.66
| 5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -17.16 | -16.47 | -15.627 | -17.88 | -17.27 | -16.4 | -15.627
| 6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.79 | -17.14 | -16.4432 | -18.71 | -18.18 | -17.1 | -16.4432
| 7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -18.32 | -17.7 | -17.1544 | -19.43 | -18.96 | -17.7 | -17.1544
| 8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -18.47 | -17.59 | -17.5283 | -19.99 | -19.56 | -17.7 | -17.5283
| 9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -15.47 | -13.46 | -14.9139 | -18.51 | -16.89 | -14.5 | -14.9139
| 10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -9.56 | -7.099 | -8.3575 | -13.56 | -11.24 | -8 | -8.3575
| 11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 0.49 | 3.657 | 1.3922 | -4.94 | -1.83 | 2.2 | 1.3922
| 12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 10.39 | 13.49 | 12.127 | 5.81 | 8.28 | 13 | 12.127
| 13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 18.75 | 21.77 | 21.2022 | 15.65 | 17.31 | 22.4 | 21.2022
| 14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 25.48 | 28.26 | 28.0199 | 23.54 | 24.69 | 30 | 28.0199
| 15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 29.21 | 32.09 | 32.1284 | 28.66 | 29.19 | 34.5 | 32.1284
| 16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 28.97 | 32.16 | 32.5897 | 30.21 | 30.2 | 35 | 32.5897
| 17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 22.58 | 25.71 | 28.2043 | 27.08 | 26.67 | 28.8 | 28.2043
| 18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 15.59 | 18.84 | 21.6872 | 20.81 | 21.04 | 21.5 | 21.6872
| 19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 10.2 | 13.1 | 15.9032 | 14.66 | 15.63 | 15.2 | 15.9032
| 20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 6.02 | 8.408 | 11.3558 | 9.46 | 10.98 | 10.1 | 11.3558
| 21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 2.39 | 4.387 | 7.0507 | 5.08 | 6.91 | 5.8 | 7.0507
| 22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | -0.59 | 0.9659 | 3.5836 | 1.39 | 3.46 | 2.2 | 3.5836
| 23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -3.04 | -1.781 | 0.6257 | -1.66 | 0.56 | -0.7 | 0.6257
| 24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -5.14 | -4.032 | -1.6964 | -4.24 | -1.95 | -3.2 | -1.6964
代表日1/4の自然室温（Case 900FF） [℃]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -2.68 | -3.455 | 0.72643 | -0.76 | -0.38 | 0.6 | 0.72643
| 2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.33 | -3.986 | 0.066993 | -1.4 | -1.09 | 0 | 0.066993
| 3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -3.72 | -4.395 | -0.45923 | -1.96 | -1.64 | -0.5 | -0.45923
| 4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.1 | -4.8 | -0.93674 | -2.45 | -2.18 | -1 | -0.93674
| 5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -4.51 | -5.216 | -1.446 | -2.94 | -2.71 | -1.5 | -1.446
| 6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -4.93 | -5.604 | -1.917 | -3.43 | -3.23 | -2 | -1.917
| 7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.34 | -5.984 | -2.3775 | -3.9 | -3.73 | -2.5 | -2.3775
| 8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -5.64 | -6.078 | -2.6597 | -4.35 | -4.21 | -2.8 | -2.6597
| 9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.59 | -4.717 | -1.649 | -3.81 | -3.61 | -2.2 | -1.649
| 10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.64 | -2.977 | 0.11787 | -2.16 | -2.22 | -0.7 | 0.11787
| 11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.75 | 0.2494 | 2.9923 | 0.43 | 0.18 | 1.7 | 2.9923
| 12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 3.26 | 2.539 | 5.4989 | 3.2 | 2.55 | 4.1 | 5.4989
| 13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.99 | 4.382 | 7.5557 | 5.1 | 4.63 | 6.2 | 7.5557
| 14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 6.51 | 5.853 | 9.2184 | 6.5 | 6.46 | 8 | 9.2184
| 15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 7.11 | 6.614 | 10.0725 | 7.21 | 7.51 | 9.1 | 10.0725
| 16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.68 | 6.333 | 9.8618 | 7.02 | 7.75 | 9.4 | 9.8618
| 17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.24 | 4.204 | 8.3893 | 5.58 | 6.84 | 8 | 8.3893
| 18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.45 | 2.869 | 6.8932 | 3.94 | 5.6 | 6.8 | 6.8932
| 19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 1.71 | 2.107 | 5.8967 | 3.1 | 4.73 | 6 | 5.8967
| 20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.32 | 1.581 | 5.1931 | 2.51 | 4.08 | 5.2 | 5.1931
| 21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 0.82 | 1.047 | 4.5093 | 1.97 | 3.44 | 4.5 | 4.5093
| 22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.42 | 0.5504 | 3.8845 | 1.46 | 2.89 | 3.9 | 3.8845
| 23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.05 | 0.1517 | 3.3882 | 1 | 2.38 | 3.4 | 3.3882
| 24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.34 | -0.238 | 2.8999 | 0.52 | 1.87 | 2.8 | 2.8999
代表日7/27の自然室温（Case 650FF） [℃]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.26 | 22.69 | 22.8217 | 23.65 | 22.39 | 22.5 | 22.8217
| 2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.11 | 21.33 | 21.3196 | 21.93 | 21 | 21.3 | 21.3196
| 3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.28 | 20.41 | 20.3591 | 20.74 | 20 | 20.4 | 20.3591
| 4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.49 | 19.61 | 19.5402 | 19.8 | 19.16 | 19.6 | 19.5402
| 5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.14 | 19.16 | 19.0164 | 19.14 | 18.74 | 19.2 | 19.0164
| 6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.81 | 19.6 | 19.3361 | 19.2 | 19.23 | 19.8 | 19.3361
| 7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 22.49 | 21.68 | 21.4065 | 20.78 | 21.6 | 22.2 | 21.4065
| 8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 24.81 | 23.47 | 23.8142 | 23.45 | 23.39 | 24.1 | 23.8142
| 9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 28.04 | 26.38 | 26.7262 | 26.87 | 26.39 | 27.4 | 26.7262
| 10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 32.11 | 30.35 | 31.098 | 31.42 | 30.22 | 31.7 | 31.098
| 11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 36.54 | 34.82 | 35.2234 | 36.61 | 34.58 | 36.5 | 35.2234
| 12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 41.15 | 39.38 | 39.8887 | 41.87 | 39.1 | 41.5 | 39.8887
| 13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 45.03 | 43.48 | 43.9853 | 46.51 | 43.21 | 45.8 | 43.9853
| 14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 47.65 | 46.14 | 47.0105 | 49.91 | 46.41 | 49 | 47.0105
| 15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 49.04 | 47.4 | 48.5663 | 51.61 | 48.24 | 50.6 | 48.5663
| 16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 49.28 | 47.33 | 48.7038 | 51.63 | 48.53 | 50.7 | 48.7038
| 17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 48.73 | 46.71 | 47.9863 | 50.73 | 47.99 | 50 | 47.9863
| 18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 46.58 | 45.28 | 46.5822 | 49.32 | 46.68 | 39.9 | 46.5822
| 19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 34.91 | 33.1 | 35.2501 | 43.01 | 36.59 | 34.4 | 35.2501
| 20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.69 | 30.49 | 31.7499 | 35.46 | 32.33 | 31.1 | 31.7499
| 21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.81 | 28.55 | 29.3277 | 31.82 | 29.54 | 28.8 | 29.3277
| 22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 27.1935 | 28.97 | 27.12 | 26.6 | 27.1935
| 23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.69 | 25.55 | 25.786 | 26.94 | 25.87 | 25.7 | 25.786
| 24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.1 | 24.26 | 24.4787 | 25.35 | 24.22 | 24.1 | 24.4787
代表日7/27の自然室温（Case 950FF） [℃]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 24.53 | 25.28 | 24.5751 | 26.15 | 24.75 | 25.2 | 24.5751
| 2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 23.8 | 24.47 | 23.6613 | 25.23 | 23.99 | 24.5 | 23.6613
| 3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.23 | 23.87 | 23.0488 | 24.58 | 23.36 | 23.8 | 23.0488
| 4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 22.6 | 23.26 | 22.4362 | 23.96 | 22.71 | 23.2 | 22.4362
| 5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.27 | 22.87 | 22.0084 | 23.46 | 22.33 | 22.8 | 22.0084
| 6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 22.67 | 23.06 | 22.1691 | 23.41 | 22.56 | 23.1 | 22.1691
| 7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.55 | 24.38 | 23.5666 | 24.34 | 24.08 | 24.7 | 23.5666
| 8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.57 | 27.21 | 26.76 | 26.26 | 25.73 | 26.9 | 26.76
| 9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 29.42 | 27.98 | 28.5614 | 28.05 | 26.84 | 27.8 | 28.5614
| 10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 30.68 | 29.11 | 30.0275 | 29.43 | 27.97 | 28.9 | 30.0275
| 11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 31.91 | 30.31 | 31.2247 | 30.82 | 29.17 | 30.1 | 31.2247
| 12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 33.27 | 31.53 | 32.3606 | 32.13 | 30.43 | 31.4 | 32.3606
| 13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 34.27 | 32.55 | 33.3769 | 33.21 | 31.54 | 32.5 | 33.3769
| 14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 34.9 | 33.15 | 34.0279 | 33.89 | 32.44 | 33.3 | 34.0279
| 15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 35.19 | 33.37 | 34.3675 | 34.13 | 32.95 | 33.8 | 34.3675
| 16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 35.28 | 33.38 | 34.4082 | 34.05 | 33.05 | 34 | 34.4082
| 17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 35.3 | 33.37 | 34.3767 | 34 | 33.03 | 34.2 | 34.3767
| 18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 34.71 | 33.16 | 34.094 | 33.94 | 32.81 | 32 | 34.094
| 19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.74 | 30.43 | 30.5381 | 32.53 | 30.57 | 30.8 | 30.5381
| 20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.38 | 29.61 | 29.4096 | 30.78 | 29.59 | 29.9 | 29.4096
| 21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 27.64 | 28.89 | 28.5729 | 29.94 | 28.78 | 29.1 | 28.5729
| 22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.46 | 27.93 | 27.5311 | 29.04 | 27.69 | 28 | 27.5311
| 23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.1 | 27.42 | 26.8874 | 28.34 | 27.31 | 27.6 | 26.8874
| 24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.02 | 26.59 | 26.0901 | 27.64 | 26.27 | 26.5 | 26.0901
代表日1/4の冷暖房負荷（Case 600） [kWh]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 4.225 | 3.7667 | 3.5735 | 3.864 | 4.199 | 3.9069 | 3.5735
| 2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 4.354 | 3.8667 | 3.693 | 3.9888 | 4.3411 | 4.0186 | 3.693
| 3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 4.321 | 3.9028 | 3.7311 | 4.0512 | 4.3282 | 4.072 | 3.7311
| 4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 4.308 | 3.8944 | 3.7401 | 4.0464 | 4.309 | 4.0488 | 3.7401
| 5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 4.303 | 3.9167 | 3.7518 | 4.0416 | 4.2979 | 4.0441 | 3.7518
| 6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 4.307 | 3.9306 | 3.7479 | 4.0368 | 4.2912 | 4.0453 | 3.7479
| 7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 4.307 | 3.9306 | 3.7478 | 4.0368 | 4.2835 | 4.0465 | 3.7478
| 8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 4.167 | 3.7528 | 3.5211 | 4.0224 | 4.2418 | 3.9976 | 3.5211
| 9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.912 | 2.4228 | 2.1269 | 3.2208 | 2.6179 | 3.3383 | 2.1269
| 10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 1.466 | 0.79667 | 0.59941 | 1.4448 | 0.5064 | 1.4128 | 0.59941
| 11 | 0.151 | 0 | 0 | 0 |  | 0 | 0 | -0.034833 | -0.071877 | 0.2304 | 0 | -0.046511 | -0.071877
| 12 | -0.771 | -1.2242 | -1.552 | -1.066 |  | -1.036 | -0.424 | -1.435 | -1.9509 | -1.1664 | -2.0942 | -0.99883 | -1.9509
| 13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.364 | -2.7203 | -3.354 | -2.8992 | -3.8261 | -3.1174 | -3.354
| 14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -2.759 | -3.1556 | -3.6172 | -3.504 | -4.1261 | -3.8918 | -3.6172
| 15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.431 | -2.8444 | -2.9636 | -3.072 | -3.3293 | -3.7709 | -2.9636
| 16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.14 | -1.7158 | -1.473 | -1.7856 | -1.6906 | -2.7186 | -1.473
| 17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | -0.020536 | -0.48 | 0 | -0.59418 | -0.020536
| 18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 1.292 | 0.77306 | 0.4236 | 0.8112 | 0.07872 | 0.21395 | 0.4236
| 19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.445 | 2.3014 | 1.8281 | 2.3184 | 2.6616 | 2.0023 | 1.8281
| 20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.941 | 2.9667 | 2.571 | 3.2304 | 3.3298 | 2.986 | 2.571
| 21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.405 | 3.2778 | 2.9766 | 3.5328 | 3.6158 | 3.3116 | 2.9766
| 22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.594 | 3.4611 | 3.1881 | 3.6192 | 3.6979 | 3.486 | 3.1881
| 23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.696 | 3.5 | 3.2464 | 3.6192 | 3.6998 | 3.5418 | 3.2464
| 24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.769 | 3.4722 | 3.2643 | 3.6144 | 3.7027 | 3.5581 | 3.2643
代表日1/4の冷暖房負荷（Case 900） [kWh]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| 1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.4 | 3.0806 | 2.6854 | 3.2112 | 3.3941 | 3.1709 | 2.6854
| 2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.547 | 3.2028 | 2.8295 | 3.36 | 3.575 | 3.3093 | 2.8295
| 3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.573 | 3.2778 | 2.9046 | 3.456 | 3.6413 | 3.4011 | 2.9046
| 4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.629 | 3.3306 | 2.9825 | 3.5136 | 3.7205 | 3.4523 | 2.9825
| 5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.687 | 3.4167 | 3.0606 | 3.5712 | 3.7925 | 3.5128 | 3.0606
| 6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.747 | 3.4694 | 3.1168 | 3.6288 | 3.8544 | 3.5686 | 3.1168
| 7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.797 | 3.5167 | 3.1744 | 3.6768 | 3.9067 | 3.6186 | 3.1744
| 8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.794 | 3.4639 | 3.0928 | 3.7104 | 3.947 | 3.65 | 3.0928
| 9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 3.168 | 2.8333 | 2.4636 | 3.2112 | 3.2842 | 3.4604 | 2.4636
| 10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.449 | 2.0561 | 1.7848 | 2.2176 | 2.3232 | 2.7686 | 1.7848
| 11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 1.293 | 0.79333 | 0.99823 | 0.888 | 0.91248 | 1.6442 | 0.99823
| 12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.619 | 0.037278 | 0.27993 | 0.0192 | 0 | 0.36162 | 0.27993
| 13 | 0.074 | 0 | 0 | 0 |  | 0 | 0.136 | 0 | 0 | 0 | 0 | -0.025581 | 0
| 14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | -0.024418 | 0
| 15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | -0.012791 | 0
| 16 | 0 | 0 | 0 | 0 |  | 0 | 0.088 | 0 | 0 | 0 | 0 | 0.0011628 | 0
| 17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 1.198 | 0.13494 | 0.12595 | 0.1488 | 0 | 0.027907 | 0.12595
| 18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 1.602 | 0.76444 | 0.61859 | 0.6384 | 0 | 0.026744 | 0.61859
| 19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.805 | 1.1986 | 0.98405 | 1.1616 | 0.48192 | 0.13488 | 0.98405
| 20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.943 | 1.4589 | 1.2301 | 1.4784 | 0.99264 | 0.67906 | 1.2301
| 21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 2.121 | 1.7008 | 1.4598 | 1.7472 | 1.3944 | 1.1442 | 1.4598
| 22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 2.227 | 1.9342 | 1.6442 | 1.9776 | 1.6973 | 1.5291 | 1.6442
| 23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.338 | 2.0922 | 1.757 | 2.1648 | 1.9522 | 1.8256 | 1.757
| 24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.458 | 2.2267 | 1.8519 | 2.3376 | 2.1898 | 2.0767 | 1.8519
自然室温頻度分布（Case 900FF） [hour]
|  | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
| -6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0
| -5 | 0 | 0 | 1 | 2 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 0 | 0
| -4 | 0 | 1 | 3 | 3 | 4 | 4 | 5 | 6 | 0 | 3 | 1 | 0 | 0
| -3 | 0 | 3 | 7 | 5 | 2 | 3 | 7 | 6 | 2 | 4 | 3 | 1 | 2
| -2 | 3 | 5 | 5 | 7 | 7 | 8 | 10 | 12 | 5 | 6 | 7 | 3 | 5
| -1 | 3 | 6 | 10 | 7 | 5 | 5 | 18 | 13 | 6 | 9 | 4 | 5 | 6
| 0 | 8 | 10 | 18 | 19 | 18 | 18 | 20 | 12 | 7 | 11 | 8 | 6 | 7
| 1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 15 | 18 | 16 | 11 | 15
| 2 | 18 | 14 | 18 | 13 | 20 | 14 | 16 | 20 | 14 | 14 | 16 | 16 | 14
| 3 | 18 | 19 | 19 | 15 | 15 | 19 | 25 | 18 | 18 | 18 | 18 | 17 | 18
| 4 | 17 | 14 | 20 | 23 | 20 | 21 | 24 | 20 | 16 | 18 | 16 | 15 | 16
| 5 | 18 | 25 | 30 | 28 | 24 | 27 | 27 | 26 | 21 | 25 | 20 | 17 | 21
| 6 | 22 | 19 | 25 | 29 | 27 | 30 | 35 | 34 | 24 | 38 | 29 | 23 | 24
| 7 | 31 | 33 | 37 | 28 | 28 | 33 | 45 | 29 | 32 | 34 | 27 | 28 | 32
| 8 | 30 | 34 | 51 | 46 | 33 | 46 | 59 | 44 | 29 | 36 | 32 | 25 | 29
| 9 | 42 | 42 | 59 | 62 | 57 | 61 | 73 | 55 | 44 | 55 | 44 | 34 | 44
| 10 | 51 | 54 | 84 | 69 | 53 | 71 | 118 | 57 | 56 | 73 | 56 | 47 | 56
| 11 | 67 | 72 | 107 | 111 | 89 | 116 | 134 | 95 | 63 | 89 | 68 | 51 | 63
| 12 | 90 | 115 | 139 | 137 | 112 | 127 | 138 | 127 | 98 | 109 | 95 | 72 | 98
| 13 | 115 | 137 | 153 | 141 | 142 | 157 | 173 | 143 | 114 | 136 | 117 | 96 | 114
| 14 | 156 | 159 | 158 | 154 | 151 | 160 | 183 | 162 | 143 | 164 | 141 | 111 | 143
| 15 | 172 | 165 | 206 | 188 | 178 | 207 | 234 | 183 | 167 | 189 | 150 | 147 | 167
| 16 | 215 | 198 | 239 | 232 | 195 | 224 | 274 | 234 | 187 | 197 | 178 | 153 | 187
| 17 | 244 | 245 | 274 | 253 | 248 | 255 | 298 | 273 | 230 | 242 | 210 | 182 | 230
| 18 | 293 | 277 | 350 | 301 | 266 | 315 | 342 | 296 | 268 | 275 | 251 | 207 | 268
| 19 | 338 | 317 | 322 | 336 | 332 | 347 | 352 | 356 | 322 | 302 | 316 | 250 | 322
| 20 | 387 | 365 | 375 | 342 | 344 | 352 | 331 | 346 | 335 | 342 | 330 | 317 | 335
| 21 | 398 | 358 | 392 | 362 | 361 | 366 | 334 | 388 | 367 | 370 | 347 | 339 | 367
| 22 | 385 | 372 | 364 | 329 | 376 | 349 | 343 | 380 | 383 | 332 | 397 | 327 | 383
| 23 | 396 | 341 | 370 | 348 | 366 | 357 | 349 | 366 | 395 | 331 | 381 | 380 | 395
| 24 | 380 | 368 | 381 | 352 | 341 | 341 | 338 | 401 | 369 | 342 | 351 | 377 | 369
| 25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 410 | 354 | 397 | 351 | 410
| 26 | 455 | 389 | 431 | 373 | 426 | 399 | 393 | 436 | 406 | 359 | 401 | 391 | 406
| 27 | 459 | 420 | 415 | 415 | 418 | 403 | 396 | 465 | 464 | 395 | 444 | 397 | 464
| 28 | 445 | 463 | 452 | 390 | 446 | 440 | 411 | 412 | 434 | 439 | 454 | 429 | 434
| 29 | 459 | 419 | 410 | 405 | 432 | 396 | 391 | 408 | 444 | 431 | 431 | 455 | 444
| 30 | 415 | 396 | 404 | 418 | 422 | 395 | 362 | 398 | 448 | 384 | 432 | 446 | 448
| 31 | 406 | 393 | 342 | 401 | 389 | 360 | 342 | 335 | 405 | 412 | 400 | 415 | 405
| 32 | 369 | 348 | 349 | 341 | 334 | 337 | 322 | 348 | 357 | 347 | 373 | 404 | 357
| 33 | 339 | 315 | 309 | 330 | 338 | 306 | 291 | 310 | 336 | 328 | 329 | 357 | 336
| 34 | 277 | 321 | 242 | 285 | 311 | 306 | 266 | 297 | 316 | 346 | 330 | 320 | 316
| 35 | 230 | 303 | 197 | 246 | 262 | 256 | 210 | 202 | 253 | 289 | 264 | 337 | 253
| 36 | 191 | 254 | 185 | 213 | 203 | 217 | 169 | 197 | 198 | 247 | 235 | 285 | 198
| 37 | 164 | 195 | 136 | 156 | 189 | 166 | 151 | 161 | 190 | 217 | 214 | 236 | 190
| 38 | 108 | 175 | 92 | 146 | 137 | 138 | 132 | 97 | 132 | 161 | 148 | 191 | 132
| 39 | 71 | 99 | 74 | 112 | 103 | 97 | 85 | 86 | 106 | 123 | 122 | 173 | 106
| 40 | 37 | 66 | 35 | 90 | 71 | 57 | 59 | 48 | 73 | 82 | 85 | 116 | 73
| 41 | 15 | 32 | 16 | 58 | 35 | 31 | 32 | 22 | 39 | 41 | 45 | 91 | 39
| 42 | 0 | 25 | 5 | 36 | 18 | 10 | 20 | 11 | 16 | 22 | 22 | 63 | 16
| 43 | 0 | 5 | 0 | 18 | 5 | 1 | 1 | 2 | 3 | 1 | 5 | 31 | 3
| 44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0
| 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
■複数室
| 冷房負荷 | kW
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
| MZN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5413 | 1.3104 | 1.3272 | 1.3337 | 1.5415
| MZA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.12 | 3.3005 | 4.1767 | 3.118
| 室温 | ℃
|  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TASE | TRNSYS | EnergyPlus | NewHASP | BEST | OFFICE | Your Program
MZN | Zone A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.06 | 30.89 | 32.62 | 33 | 31.0587
| Zone B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8 | 24.7 | 25.62 | 25.8 | 24.7984
| Zone C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15 | 15
MZA | Zone A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.44 | 25.2 | 21.82 | 25.7323
| Zone B | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 21.15 | 18.89 | 21.4658
| Zone C | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15